## AMAT
PO | PROJECT | CHEMICAL | CHEM NAME | PLC IP | HMI IP | Subnet Mask | Gateway | MODEL | PROGRAM | INSTALLED VER | WIP VER | DELIVERY | COMMISSIONED | STATUS | SHIPPED | ProgSent | Notes
4400596118 | D23278 | IPA | Isopropyl Alcohol | 192.168.0.1 | 192.168.0.2 | 255.255.255.0 | None | DFS ACvFLO Compact Automatic IPA Liquid Dispense System |  |  |  | 2021-11-12 |  | SHIPPED | 2022-02-25 | NO
Note on M1: Requested Date
Note on O1: QUOTED DESIGN LOADED SHIPPED
Note on P1: Actual date

## MTI GC
PO | PROJECT | GAS | GAS NAME | BLDG | PLC HOSTNAME | PLC IP | HMI IP | Subnet Mask | Gateway | GC# | MODEL | PROGRAM | INS VER | WIP VER | DELIVERY | COMMISSION | STATUS | SHIPPED | ProgSent | Notes
4505449232 | D10410-001 | CH4 | Methane | B03 | G13B05B06 | 172.19.7.49 | 172.19.7.50 | 255.255.0.0 | 172.19.0.250 | GC1355 | DFS 1-AX250-CH4 | DISC | V17.0.6.115.5 | V17.0.6.115.5 | 2016-11-23 |  | SHIPPED | 2016-11-23 | 2023-07-13 | _6B 7/13/23 upd
4505750567 | D10513-001 | TSA | Trisilylamine | B50 SF | GC5092 | 172.19.7.77 | 172.19.7.78 | 255.255.0.0 | 172.19.0.250 | GC5092 | DFS 4-AX250-TSA | DISC* | V14.1.3.099 | V15.0.4.110 | 2017-03-03 |  | SHIPPED | 2017-03-03 | 2017-03-07 | *Control cabinet to be replaced with ASD.
4505753842 | D10521-003 | CH2F2 | Difluoromethane | B51 Pyro | G55C03C04 | 172.19.7.93 | 172.19.7.94 | 255.255.0.0 | 172.19.0.250 | GC5525 | DFS 1-AX250-CH2F2 | DISC | V17.0.5.115.5 | V17.0.5.115.5 | 2017-06-08 |  | SHIPPED | 2017-06-08 | 2023-06-23 | _6B 6/22/23 upd
4505753842 | D10521-004 | C4F6 | Hexafluorocyclobutene | B51 Pyro | G55C05C06 | 172.19.7.95 | 172.19.7.96 | 255.255.0.0 | 172.19.0.250 | GC5526 | DFS 1-AX250-C4F6 | DISC | V17.0.5.115.5 | V17.0.5.115.5 | 2017-06-08 |  | SHIPPED | 2017-06-08 | 2023-06-23 | _6B 6/22/23 upd
4505753842 | D10521-005 | COS | Carbonyl Sulfide | B51 Pyro | G55C09C10 | 172.19.7.105 | 172.19.7.106 | 255.255.0.0 | 172.19.0.250 | GC5528 | DFS 1-AX250-COS | DISC | V17.0.6.115.5 | V17.0.6.115.5 | 2017-06-08 |  | SHIPPED | 2017-06-08 | 2023-06-30 | _6B 7/27/23 upd
4505753842 | D10521-006 | SiH4 | Silane | B51 Pyro | G55C01C02 | 172.19.7.99 | 172.19.7.100 | 255.255.0.0 | 172.19.0.250 | GC5524 | DFS 1-AX250-SiH4 | DISC | V17.0.5.115.5 | V17.0.5.115.5 | 2017-06-08 |  | SHIPPED | 2017-06-08 | 2023-03-31 | _6B 3/30/23 upd. Need to update cert
4505753842 | D10521-007 | CO | Carbon Monoxide | B51 Pyro | G55C07C08 | 172.19.7.103 | 172.19.7.104 | 255.255.0.0 | 172.19.0.250 | GC5527 | DFS 1-AX250-CO | DISC | V17.0.5.115.5 | V17.0.5.115.5 | 2017-06-08 |  | SHIPPED | 2017-06-08 | 2023-06-23 | _6B 6/22/23 upd
4505801887 | D10541-001 | CH4 | Methane | B51 Pyro | G55C13C14 | 172.19.7.87 | 172.19.7.88 | 255.255.0.0 | 172.19.0.250 | GC5530 | DFS 1-AX250-CH4 | DISC | V17.0.6.115.5 | V17.0.6.115.5 | 2017-06-29 |  | SHIPPED | 2017-06-29 | 2023-06-30 | _6B 7/27/23 upd
4505801887 | D10541-002 | Cl2 | Chlorine | B51 Oxid | G53B05B06 | 172.19.7.83 | 172.19.7.84 | 255.255.0.0 | 172.19.0.250 | GC5321 | DFS 1-AX250-Cl2 | DISC | V17.0.6.115.5 | V17.0.6.115.5 | 2017-06-29 | 2017-11-01 | SHIPPED | 2017-06-29 | 2023-09-15 | _6B upd 9/14/23
4505801887 | D10541-003 | HBr | Hydrogen Bromide | B51 Oxid | G53B07B08 | 172.19.7.85 | 172.19.7.86 | 255.255.0.0 | 172.19.0.250 | GC5322 | DFS 1-AX250-HBr | DISC | V17.0.6.115.5 | V17.0.6.115.5 | 2017-06-29 | 2017-10-03 | SHIPPED | 2017-06-29 | 2023-09-15 | _6B upd 9/14/23
4505801887 | D10541-004 | CH3F | Fluoromethane (Halocarbon-41) | B51 Pyro | G55C11C12 | 172.19.7.81 | 172.19.7.82 | 255.255.0.0 | 172.19.0.250 | GC5529 | DFS 1-AX250-CH3F | DISC | V17.0.6.115.5 | V17.0.6.115.5 | 2017-06-29 |  | SHIPPED | 2017-06-29 | 2023-06-30 | _6B 7/27/23 upd
4505801887 | D10541-005 | BCl3 | Boron Trichloride | B51 Oxid | G53B09B10 | 172.19.7.89 | 172.19.7.90 | 255.255.0.0 | 172.19.0.250 | GC5323 | DFS 1-AX250-BCl3 | DISC | V17.0.6.115.5 | V17.0.6.115.5 | 2017-06-29 | 2017-11-01 | SHIPPED | 2017-06-29 | 2023-09-15 | _6B upd 9/14/23
4505801887 | D10541-006 | SO2 | Sulfur Dioxide | B51 Oxid | G53B11B12 | 172.19.7.91 | 172.19.7.92 | 255.255.0.0 | 172.19.0.250 | GC5324 | DFS 1-AX250-SO2 | DISC | V17.0.6.115.5 | V17.0.6.115.5 | 2017-06-29 | 2017-11-01 | SHIPPED | 2017-06-29 | 2023-09-15 | _6B upd 9/14/23
4505886873 | D10560-001 | C2H2 | Acetylene | B24D SF | GC9031 | 172.19.7.75 | 172.19.7.76 | 255.255.0.0 | 172.19.0.250 | GC9031 | DFS 1-AX250-C2H2 | DISC PIGTAIL PURGE | V15.0.4.115 | V17.0.6.115.5A | 2017-08-17 | UNK | SHIPPED | 2017-08-17 | 2021-05-11 | _F7 Needs new wip
4505905865 | D10569-001 | F2 20%/Ar | Fluorine(20%) / Argon | B51 Oxid | G53B23B24 | 172.19.7.108 | 172.19.7.109 | 255.255.0.0 | 172.19.0.250 | GC5330 | DFS 1-AX250-F2 20%/Ar | DISC | V17.0.6.115.5 | V17.0.6.115.5 | 2017-08-11 | 2018-02-21 | SHIPPED | 2017-08-11 | 2019-07-26 | _6B upd 10/12/23
4505905865 | D10569-002 | BF3 | Boron Trifluoride | B51 Oxid | G53B29B30 | 172.19.7.110 | 172.19.7.111 | 255.255.0.0 | 172.19.0.250 | GC5333 | DFS 1-AX250-BF3 | DISC | V17.0.6.115.5 | V17.0.6.115.5 | 2017-08-17 |  | SHIPPED | 2017-08-17 | 2019-07-26 | _6B upd 10/12/23
4505905865 | D10569-003 | ClF3 | Chlorine Trifluoride | B51 Oxid | G53B13B14 | 172.19.7.112 | 172.19.7.113 | 255.255.0.0 | 172.19.0.250 | GC5325 | DFS 2-AX250-ClF3 | ASD | V15.0.4.110 | V17.0.6.116.5 | 2017-08-11 | 2018-01-19 | SHIPPED | 2017-08-11 | 2019-07-19 | _C5 wip
4505905865 | D10569-004 | SiH4 | Silane | B51 Pyro | G55B23B24 | 172.19.7.114 | 172.19.7.115 | 255.255.0.0 | 172.19.0.250 | GC5523 | DFS 1-AX250-SiH4 | DISC | V17.0.5.115.5 | V17.0.5.115.5 | 2017-08-17 | 2018-02-16 | SHIPPED | 2017-08-17 | 2023-03-31 | _6B 3/30/23 upd. Need to update cert
4506148181 | D10649-001 | HF | Hydrogen Fluoride | B50 SF | GC57238 | 172.19.7.158 | 172.19.7.159 | 255.255.0.0 | 172.19.0.250 | GC5029 | DFS 1-AX250-HF | DISC | V14.1.3.100 | V17.0.6.115.5 | 2017-11-21 | 2018-04-25 | SHIPPED | 2017-11-21 | 2018-05-07 | 8/23 no power WAS B51 SF GC57 238
4506148111 | D10649-002 | C2H2 | Acetylene | B51 Pyro | G55A13A14 | 172.19.7.154 | 172.19.7.155 | 255.255.0.0 | 172.19.0.250 | GC5506 | DFS 1-AX250-C2H2 | DISC PIGTAIL PURGE | V17.0.5.115.5A | V17.0.5.115.5A | 2017-12-01 | UNK | SHIPPED | 2017-12-01 | 2021-05-11 | _F7 5/11/23 upd
4506148125 | D10649-003 | DCS | Dichlorosilane (DCS) | B51 Pyro | G55B07B08 | 172.19.7.156 | 172.19.7.157 | 255.255.0.0 | 172.19.0.250 | GC5515 | DFS 1-AX250-DCS | DISC | V17.0.5.115.5 | V17.0.5.115.5 | 2017-11-21 | 2018-02-19 | SHIPPED | 2017-11-21 | 2023-03-31 | _6B 3/30/23 upd. Need to update cert
4506148139 | D10649-004 | F2 20%/N2 | Fluorine(20%) / Nitrogen | B51 Oxid | G53B15B16 | 172.19.7.160 | 172.19.7.161 | 255.255.0.0 | 172.19.0.250 | GC5326 | DFS 1-AX250-F2 20%/N2 | DISC | V17.0.6.115.5 | V17.0.6.115.5 | 2017-11-21 | 2018-02-14 | SHIPPED | 2017-11-21 | 2023-09-15 | _6B upd 9/14/23
4506148203 | D10649-005 | HF | Hydrogen Fluoride | B50 SF | GC5024 | 172.19.7.166 | 172.19.7.167 | 255.255.0.0 | 172.19.0.250 | GC5024 | DFS 1-AX250-HF | DISC | V15.0.4.110 | V17.0.6.115.5 | 2017-12-13 | 2018-03-26 | SHIPPED | 2017-12-13 | 2018-10-05 | 8/23 upd
4506148212 | D10649-006 | NO | Nitric Oxide | B51 Oxid | G53B17B18 | 172.19.7.162 | 172.19.7.163 | 255.255.0.0 | 172.19.0.250 | GC5327 | DFS 1-AX250-NO | DISC | V17.0.6.115.5 | V17.0.6.115.5 | 2017-12-15 | 2018-02-15 | SHIPPED | 2017-12-15 | 2023-09-15 | _6B upd 9/14/23
4506252621 | D10678-001 | WF6 | Tungsten Hexafluoride | B51 SF | GC57253 | 172.19.7.215 | 172.19.7.216 | 255.255.0.0 | 172.19.0.250 | GC57 253 | DFS 1-AX250-WF6 | DISC | V15.0.4.110 | V17.0.6.115.5 | 2018-01-30 | 2018-03-12 | SHIPPED | 2018-01-30 | 2018-01-29 | 8/23 upd
4506252626 | D10678-002 | WF6 | Tungsten Hexafluoride | B51 SF | GC57254 | 172.19.7.219 | 172.19.7.220 | 255.255.0.0 | 172.19.0.250 | GC57 254 | DFS 1-AX250-WF6 | DISC | V15.0.4.110 | V17.0.6.115.5 | 2018-01-30 | 2018-03-13 | SHIPPED | 2018-01-30 | 2018-01-29 | 8/23 upd changed proj ip to 219/220
4506252636 | D10678-003 | WF6 | Tungsten Hexafluoride | B51 SF | GC57255 | 172.19.7.217 | 172.19.7.218 | 255.255.0.0 | 172.19.0.250 | GC57 255 | DFS 1-AX250-WF6 | DISC | V15.0.4.110 | V17.0.6.115.5 | 2018-01-30 | 2018-03-13 | SHIPPED | 2018-01-30 | 2018-01-29 | 8/23 upd changed proj ip to 217/218
4506252692 | D10678-004 | C2H2 | Acetylene | B51 Pyro | G55A15A16 | 172.19.7.221 | 172.19.7.222 | 255.255.0.0 | 172.19.0.250 | GC5507 | DFS 1-AX250-C2H2 | DISC PIGTAIL PURGE | V17.0.5.115.5A | V17.0.5.115.5A | 2018-01-21 | 2018-02-20 | SHIPPED | 2018-01-21 | 2021-05-11 | _F7 5/11/23 upd
4506458108 | D10678-005 | HF | Hydrogen Fluoride | B51 SF | GC57278 | 172.19.8.0 | 172.19.8.1 | 255.255.0.0 | 172.19.0.250 | GC57 278 | DFS 2-AX250-HF-HEAT | DISC | V15.0.1.099.H | V17.0.6.115.5H | 2018-02-25 |  | SHIPPED | 2018-02-25 | 2018-02-26
4506478744 | D10678-006 | WF6 | Tungsten Hexafluoride | B50 SF | GC57247 | 172.19.8.19 | 172.19.8.20 | 255.255.0.0 | 172.19.0.250 | GC5071 | DFS 1-AX250-WF6 | ASD | V15.0.4.114 | V17.0.6.116.5H | 2018-03-16 | 2018-05-18 | SHIPPED | 2018-03-16 | 2018-03-14 | _F9 Need new wip
4506252717 | D10678-007 | CH2F2 | Difluoromethane | B51 Pyro | G55B01B02 | 172.19.7.233 | 172.19.7.234 | 255.255.0.0 | 172.19.0.250 | GC5512 | DFS 1-AX250-CH2F2 | DISC | V17.0.5.115.5 | V17.0.5.115.5 | 2018-02-08 | 2018-03-06 | SHIPPED | 2018-02-08 | 2023-06-23 | _6B 6/22/23 upd
4506478614 | D10678-008 | HI | Hydrogen Iodide | B51 SF | D10678-008 | 172.19.8.21 | 172.19.8.22 | 255.255.0.0 | 172.19.0.250 | GC57 206 | DFS 1-AX250-HI | ASD+RFID | V16.0.4.115 | V16.0.4.115 | 2018-03-20 | 2021-08-06 | SHIPPED | 2021-07-27 | 2021-07-28 | 7/28/21 gas changed to HI with RF610R per D22245, RFID IP is 172.19.10.16 D10678-008-RFID
4506478694 | D10678-009 | ClF3 | Chlorine Trifluoride | B51 Oxid | G53A31A32 | 172.19.8.23 | 172.19.8.24 | 255.255.0.0 | 172.19.0.250 | GC5316 | DFS 2-AX250-ClF3 | ASD | V15.0.4.110 | V17.0.6.116.5 | 2018-03-20 | 2018-06-21 | SHIPPED | 2018-03-20 | 2019-07-19 | _C5 wip
4506252749 | D10678-010 | HBr | Hydrogen Bromide | B51 Oxid | G53B21B22 | 172.19.7.235 | 172.19.7.236 | 255.255.0.0 | 172.19.0.250 | GC5329 | DFS 1-AX250-HBr | DISC | V17.0.6.115.5 | V17.0.6.115.5 | 2018-02-08 | 2018-03-06 | SHIPPED | 2018-02-08 | 2023-09-15 | _6B upd 9/14/23
4506252771 | D10678-011 | C4F6 | Hexafluorocyclobutene | B51 Pyro | G55B19B20 | 172.19.7.237 | 172.19.7.238 | 255.255.0.0 | 172.19.0.250 | GC5521 | DFS 1-AX250-C4F6 | DISC | V17.0.5.115.5 | V17.0.5.115.5 | 2018-03-13 | 2018-04-23 | SHIPPED | 2018-03-13 | 2019-06-14 | _6B 5/11/23 upd
4506252817 | D10678-012 | SiH4 | Silane | B51 Pyro | G55B21B22 | 172.19.7.239 | 172.19.7.240 | 255.255.0.0 | 172.19.0.250 | GC5522 | DFS 1-AX250-SiH4 | DISC | V17.0.5.115.5 | V17.0.5.115.5 | 2018-02-15 | 2018-03-20 | SHIPPED | 2018-02-15 | 2023-03-31 | _6B 3/30/23 upd. Need to update cert
4506458115 | D10678-013 | HF | Hydrogen Fluoride | B51 SF | GC57277 | 172.19.8.9 | 172.19.8.10 | 255.255.0.0 | 172.19.0.250 | GC57 277 | DFS 2-AX250-HF-HEAT | DISC | V15.0.1.099.H | V17.0.6.115.5H | 2018-02-25 | 2018-08-02 | SHIPPED | 2018-02-25 | 2018-02-26
4506252825 | D10678-014 | CCR | Organofluorine (CCR) | B50 SF | D10678-014 | 172.19.8.13 | 172.19.8.14 | 255.255.0.0 | 172.19.0.250 | GC5070 | DFS 1-AX250-CCR | DISC | V15.0.4.114 | V17.0.6.115.5 | 2018-02-15 | 2020-09-16 | SHIPPED | 2018-02-15 | 2020-09-16 | 9/16/20 upd changed gas to CCR (proprietary organofluorine)
4506478732 | D10678-015 | SiF4 | Silicon Tetrafluoride | B51 Oxid | G53A29A30 | 172.19.7.241 | 172.19.7.242 | 255.255.0.0 | 172.19.0.250 | GC5315 | DFS 1-AX250-SiF4 | DISC | V15.0.4.110 | V17.0.6.115.5 | 2018-04-06 | 2018-05-08 | SHIPPED | 2018-04-06 | 2019-07-19 | _6B wip
4506252829 | D10678-016 | Si2H6 | Disilane | B51 Pyro | G55B15B16 | 172.19.7.243 | 172.19.7.244 | 255.255.0.0 | 172.19.0.250 | GC5519 | DFS 1-AX250-Si2H6 | DISC | V17.0.5.115.5 | V17.0.5.115.5 | 2018-02-22 | 2018-04-11 | SHIPPED | 2018-02-22 | 2023-03-31 | _6B 3/30/23 upd
4506478508 | D10678-017 | BCl3 | Boron Trichloride | B51 Oxid | G53A27A28 | 172.19.8.25 | 172.19.8.26 | 255.255.0.0 | 172.19.0.250 | GC5314 | DFS 1-AX250-BCl3 | DISC | V17.0.6.115.5 | V17.0.6.115.5 | 2018-05-14 | 2018-06-14 | SHIPPED | 2018-05-14 | 2023-09-15 | _6B upd 9/14/23
4506252834 | D10678-018 | ClF3 | Chlorine Trifluoride | B51 Oxid | G53A33A34 | 172.19.7.245 | 172.19.7.246 | 255.255.0.0 | 172.19.0.250 | GC5317 | DFS 2-AX250-ClF3 | ASD | V15.0.4.110 | V17.0.6.116.5 | 2018-02-22 |  | SHIPPED | 2018-02-22 | 2019-07-19 | _C5 wip
4506252837 | D10678-019 | CH4 10%/Ar | Methane(10%) / Argon (P10) | B51 Pyro | G55B03B04 | 172.19.7.247 | 172.19.7.248 | 255.255.0.0 | 172.19.0.250 | GC5513 | DFS 1-AX250-CH4 10%/Ar | DISC | V17.0.5.115.5 | V17.0.5.115.5 | 2018-04-06 | 2018-05-07 | SHIPPED | 2018-04-06 | 2023-06-23 | _6B 6/22/23 upd
4506252839 | D10678-020 | B2H6 1%/H2 | Diborane(1%) / Hydrogen | B51 Pyro | G55B11B12 | 172.19.8.11 | 172.19.8.12 | 255.255.0.0 | 172.19.0.250 | GC5517 | DFS 1-AX250-B2H6 1%/H2 | DISC | V17.0.5.115.5 | V17.0.5.115.5 | 2018-02-22 | 2018-04-12 | SHIPPED | 2018-02-22 | 2023-06-23 | _6B 6/22/23 upd
4506252846 | D10678-021 | B2H6 5%/N2 | Diborane(5%) / Nitrogen | B51 Pyro | G55B09B10 | 172.19.7.249 | 172.19.7.250 | 255.255.0.0 | 172.19.0.250 | GC5516 | DFS 1-AX250-B2H6 5%/N2 | DISC | V17.0.5.115.5 | V17.0.5.115.5 | 2018-02-08 | 2018-03-20 | SHIPPED | 2018-02-08 | 2023-06-23 | _6B 6/22/23 upd
4506252845 | D10678-022 | B2H6 15%/H2 | Diborane(15%) / Hydrogen | B51 Pyro | G55B05B06 | 172.19.7.251 | 172.19.7.252 | 255.255.0.0 | 172.19.0.250 | GC5514 | DFS 1-AX250-B2H6 15%/H2 | DISC | V17.0.5.115.5 | V17.0.5.115.5 | 2018-03-07 | 2018-04-23 | SHIPPED | 2018-03-07 | 2023-06-23 | _6B 6/22/23 upd
4506478483 | D10678-023 | F2 20%/N2 | Fluorine(20%) / Nitrogen | B51 Oxid | D10678-023 | 172.19.8.27 | 172.19.8.28 | 255.255.0.0 | 172.19.0.250 | GC5308 | DFS 1-AX250-F2 20%/N2 | DISC | V17.0.6.115.5 | V17.0.6.115.5 | 2018-06-01 | 2020-04-09 | SHIPPED | 2018-06-01 | 2023-09-07 | _6B upd 9/7/23
4506478494 | D10678-024 | CH3F | Fluoromethane (Halocarbon-41) | B51 Pyro | G55C15C16 | 172.19.8.29 | 172.19.8.30 | 255.255.0.0 | 172.19.0.250 | GC5531 | DFS 1-AX250-CH3F | DISC | V17.0.5.115.5 | V17.0.5.115.5 | 2018-04-16 | 2018-06-08 | SHIPPED | 2018-04-16 | 2023-06-30 | _6B 6/29/23 upd
4506478707 | D10678-025 | Cl2 | Chlorine | B51 Oxid | G53B19B20 | 172.19.8.31 | 172.19.8.32 | 255.255.0.0 | 172.19.0.250 | GC5328 | DFS 1-AX250-Cl2 | DISC | V17.0.6.115.5 | V17.0.6.115.5 | 2018-06-01 | 2018-07-19 | SHIPPED | 2018-06-01 | 2023-09-15 | _6B upd 9/14/23
4506633225 | D10678-026 | F2 20%/N2 | Fluorine(20%) / Nitrogen | B51 Oxid | G53A25A26 | 172.19.8.33 | 172.19.8.34 | 255.255.0.0 | 172.19.0.250 | GC5313 | DFS 1-AX250-F2 20%/N2 | DISC | V17.0.6.115.5 | V17.0.6.115.5 | 2018-07-06 | 2018-08-29 | SHIPPED | 2018-07-06 | 2023-09-07 | _6B upd 9/7/23
4506522776 | D10678-027 | HF | Hydrogen Fluoride | B51 SF | D10678-027 | 172.19.8.35 | 172.19.8.36 | 255.255.0.0 | 172.19.0.250 | GC57 228 | DFS 1-AX250-HF | DISC | V15.0.4.110 | V17.0.6.115.5 | 2018-07-06 | 2019-06-26 | SHIPPED | 2018-07-06 | 2018-10-03 | 9/19 upd
4506478722 | D10678-028 | HI | Hydrogen Iodide | B51 SF | GC57239 | 172.19.8.37 | 172.19.8.38 | 255.255.0.0 | 172.19.0.250 | GC57 239 | DFS 1-AX250-HI | ASD+RFID | V16.0.2.114 | V16.0.4.114 | 2020-05-08 | 2020-05-19 | SHIPPED | 2020-05-08 | 2020-05-08 | 8/18/20 update. 2/28/20 changed gas to HI, was HF. Will be upgraded to GC57239 ASD with RF610R per D17195, RFID IP is 172.19.9.91 GC57239-RFID
4506458135 | D10690-003 | BF3 | Boron Trifluoride | B24B | GC4006 | 172.19.8.43 | 172.19.8.44 | 255.255.0.0 | 172.19.0.250 | GC4006 | DFS 1-AX250-BF3 | DISC | V15.0.4.110 | V17.0.6.115.5 | 2018-03-16 | 2018-06-03 | SHIPPED | 2018-03-16 | 2018-06-28 | 8/23 upd
4506428367 | D10728-001 | H2 | Hydrogen | B03 | G13A03A04 | 172.19.8.53 | 172.19.8.54 | 255.255.0.0 | 172.19.0.250 | GC1353 | DFS 1-AX250-H2 | DISC | V17.0.5.115.5 | V17.0.5.115.5 | 2018-04-11 | 2018-06-08 | SHIPPED | 2018-04-11 | 2023-03-24 | _6B 3/23/23 upd. Need to update cert
4506633486 | D11310-001 | Garnet | GARNET | B51 Pyro | D11310-001 | 172.19.8.127 | 172.19.8.128 | 255.255.0.0 | 172.19.0.250 | GC5552 | DFS 1-AX250-Garnet | DISC | V17.0.6.115.5 | V17.0.6.115.5 | 2018-07-17 | 2020-10-22 | SHIPPED | 2018-07-17 | 2023-08-10 | _6B 8/10/23 upd
4506633518 | D11310-003 | SiH4 | Silane | B51 Pyro | G55C19C20 | 172.19.8.57 | 172.19.8.58 | 255.255.0.0 | 172.19.0.250 | GC5533 | DFS 1-AX250-SiH4 | DISC | V17.0.6.115.5 | V17.0.6.115.5 | 2018-07-09 | 2018-08-23 | SHIPPED | 2018-07-09 | 2023-03-31 | _6B 7/27/23 upd
4506633532 | D11310-004 | TMS | Trimethylsilane | B51 Pyro | G55B17B18 | 172.19.8.59 | 172.19.8.60 | 255.255.0.0 | 172.19.0.250 | GC5520 | DFS 1-AX250-TMS | ASD | V17.0.5.116.5 | V17.0.6.116.5 | 2018-08-10 | 2018-09-10 | SHIPPED | 2018-08-10 | 2019-06-14 | _C5 5/11/23 upd | CGA 350
4506633534 | D11310-005 | HF | Hydrogen Fluoride | B51 SF | GC57268 | 172.19.8.61 | 172.19.8.62 | 255.255.0.0 | 172.19.0.250 | GC57 268 | DFS 2-AX250-HF-HEAT | DISC | V15.0.1.109.H | V17.0.6.115.5H | 2018-07-02 | 2018-08-30 | SHIPPED | 2018-07-02 | 2018-10-05
4506635040 | D11310-006 | HF | Hydrogen Fluoride | B51 SF | GC57269 | 172.19.8.63 | 172.19.8.64 | 255.255.0.0 | 172.19.0.250 | GC57 269 | DFS 2-AX250-HF-HEAT | DISC | V15.0.1.109.H | V17.0.6.115.5H | 2018-07-09 | 2018-08-29 | SHIPPED | 2018-07-09 | 2018-10-05
4506635046 | D11310-007 | WF6 | Tungsten Hexafluoride | B51 Oxid | D11310-007 | 172.19.8.131 | 172.19.8.132 | 255.255.0.0 | 172.19.0.250 | GC5357 | DFS 1-AX250-WF6 | ASD | V15.0.4.110 | V17.0.6.116.5 | 2018-08-10 | 2022-03-07 | SHIPPED | 2018-08-10 | 2019-07-01 | _C5 wip
4506633528 | D11310-008 | SiH4 | Silane | B01X | D11310-008 | 172.19.8.133 | 172.19.8.134 | 255.255.0.0 | 172.19.0.250 | SPARE | DFS 1-AX250-SiH4 | ASD | V15.0.4.110 | V17.0.6.116.5 | 2018-07-17 |  | SHIPPED | 2018-07-17 | 2019-07-01 | _C5 Need new wip
4506635052 | D11310-009 | TBD |  |  | D11310-009 | 172.19.8.135 | 172.19.8.136 | 255.255.0.0 | 172.19.0.250 | SPARE | DFS 1-AX250-TBD | ASD | V15.0.4.110 | V17.0.6.116.5 | 2018-07-25 | UNK | SHIPPED | 2018-07-25 | 2021-11-01 | _C5 Need new wip
4506635058 | D11310-010 | DCS | Dichlorosilane (DCS) | B01X | D11310-010 | 172.19.8.137 | 172.19.8.138 | 255.255.0.0 | 172.19.0.250 | SPARE | DFS 1-AX250-DCS | ASD | V15.0.4.110 | V17.0.6.116.5 | 2018-07-27 |  | SHIPPED | 2018-07-27 | 2019-07-01 | _C5 Need new wip
4506633500 | D11310-011 | F2 20%/N2 | Fluorine(20%) / Nitrogen | B51 Oxid | D11310-011 | 172.19.8.139 | 172.19.8.140 | 255.255.0.0 | 172.19.0.250 | GC5332 | DFS 1-AX250-F2 20%/N2 | ASD | V17.0.6.116.5 | V17.0.6.116.5 | 2018-07-20 | 2022-04-10 | SHIPPED | 2018-07-20 | 2022-04-14 | _C5 upd 10/12/23
4506635062 | D11310-012 | TBD |  | B01X | D11310-012 | 172.19.8.141 | 172.19.8.142 | 255.255.0.0 | 172.19.0.250 | SPARE | DFS 1-AX250-TBD | ASD | V15.0.4.115 | V17.0.6.116.5 | 2018-07-20 | UNK | SHIPPED | 2018-07-20 | 2021-11-01 | _C5 Need new wip
4506698712 | D11310-013 | CH4 | Methane | B51 Pyro | G55C17C18 | 172.19.8.97 | 172.19.8.98 | 255.255.0.0 | 172.19.0.250 | GC5532 | DFS 1-AX250-CH4 | ASD | V17.0.6.116.5 | V17.0.6.116.5 | 2018-07-25 | 2018-09-07 | SHIPPED | 2018-07-25 | 2023-06-30 | _C5 7/27/23 upd
4506798828 | D11634-001 | TSA | Trisilylamine | B51 SF | GC57241 | 172.19.8.66 | 172.19.8.67 | 255.255.0.0 | 172.19.0.250 | GC57 241 | DFS 2-AX250-TSA | ASD | V15.0.4.110 | V17.0.6.116.5 | 2018-07-17 | 2018-09-14 | SHIPPED | 2018-07-17 | 2018-10-05 | _C5 Need new wip
4506783663 | D11827-001 | ClF3 | Chlorine Trifluoride | B51 Oxid | G53A23A24 | 172.19.8.143 | 172.19.8.144 | 255.255.0.0 | 172.19.0.250 | GC5312 | DFS 2-AX250-ClF3 | ASD | V15.0.4.110 | V17.0.6.116.5 | 2018-08-01 | 2018-11-19 | SHIPPED | 2018-08-01 | 2019-07-19 | _C5 wip
4506863124 | D11992-001 | Garnet | GARNET | B51 Pyro | D11992-001 | 172.19.8.147 | 172.19.8.148 | 255.255.0.0 | 172.19.0.250 | GC5551 | DFS 1-AX250-Garnet | ASD | V17.0.6.116.5 | V17.0.6.116.5 | 2018-09-27 | 2020-12-17 | SHIPPED | 2018-09-27 | 2023-08-10 | _C5 8/10/23 upd
4506861323 | D11992-002 | CH3OH | Methanol(MEOH) | B51 SF | GC57227 | 172.19.8.99 | 172.19.8.100 | 255.255.0.0 | 172.19.0.250 | GC57 227 j24 | DFS 2-AX250-CH3OH-HEAT | ASD | V17.0.6.116.5H | V17.0.6.116.5H | 2018-09-19 | 2019-10-23 | SHIPPED | 2018-09-19 | 2023-07-19 | _F9 7/19/23 upd,1/28/22 Upgraded via D21512-001 and added Panel Heat Was originally shipped as D10678-006
4506861520 | D11992-003 | CH3I | Methyl Iodide | B51 SF | GC57230 | 172.19.8.101 | 172.19.8.102 | 255.255.0.0 | 172.19.0.250 | GC57 230 | DFS 2-AX250-CH3I-HEAT | ASD | V15.0.4.110.H | V17.0.6.116.5H | 2018-09-19 | 2020-02-27 | SHIPPED | 2018-09-19 | 2018-09-24 | _F9 Need new wip Orig PO 4506861520 HF+heat, 9/19 upd, 2/27 changed GC57263 to GC57230 and gas to CH3I
4506861537 | D11992-004 | PF3 | Phosphorus Trifluoride | B51 Oxid | GC9026 | 172.19.8.103 | 172.19.8.104 | 255.255.0.0 | 172.19.0.250 | GC5358 | DFS 1-AX250-PF3 | ASD | V15.0.4.110 | V17.0.6.116.5 | 2018-09-25 | 2018-11-15 | SHIPPED | 2018-09-25 | 2019-08-03 | _C5 wip
4506863123 | D11992-005 | HBr | Hydrogen Chloride | B51 Oxid | G53A21A22 | 172.19.8.105 | 172.19.8.106 | 255.255.0.0 | 172.19.0.250 | GC5301 | DFS 1-AX250-HBr | ASD | V17.0.6.116.5 | V17.0.6.116.5 | 2018-09-25 | 2022-04-05 | SHIPPED | 2018-09-25 | 2023-09-07 | _C5 upd 9/7/23
4506863099 | D11992-006 | DCS | Dichlorosilane (DCS) | B51 SF | GC9027 | 172.19.8.107 | 172.19.8.108 | 255.255.0.0 | 172.19.0.250 | GC57 244 | DFS 1-AX250-DCS | ASD | V15.0.4.110 | V17.0.6.116.5 | 2018-09-27 | 2018-11-15 | SHIPPED | 2018-09-27 | 2019-08-03 | _C5 Need new wip
4506861709 | D11992-007 | PH3 .5%/N2 | Phosphine(0.5%) / Nitrogen | B51 Pyro | G55C21C22 | 172.19.8.109 | 172.19.8.110 | 255.255.0.0 | 172.19.0.250 | GC5534 | DFS 1-AX250-PH3 .5%/N2 | ASD | V17.0.6.116.5 | V17.0.6.116.5 | 2018-09-27 | 2018-11-08 | SHIPPED | 2018-09-27 | 2023-06-30 | _C5 7/27/23 upd
4507267384 | D13689-001 | B2H6 10%/H2 | Diborane(10%) / Hydrogen | B51 Pyro | D13689-001 | 172.19.8.174 | 172.19.8.175 | 255.255.0.0 | 172.19.0.250 | GC5535 | DFS 1-AX250-B2H6 10%/H2 | ASD | V17.0.6.116.5 | V17.0.6.116.5 | 2018-12-28 | 2019-02-25 | SHIPPED | 2018-12-28 | 2023-06-30 | _C5 7/27/23 upd
4507267394 | D13689-002 | C3H6 | Propylene | B51 Pyro | D13689-002 | 172.19.8.176 | 172.19.8.177 | 255.255.0.0 | 172.19.0.250 | GC5545 | DFS 1-AX250-C3H6 | ASD | V17.0.6.116.5 | V17.0.6.116.5 | 2018-12-28 | 2019-02-25 | SHIPPED | 2018-12-28 | 2023-07-13 | _C5 7/27/23 upd
4507362959 | D14204-001 | ClF3 | Chlorine Trifluoride | B01X | D14204-001 | 172.19.8.39 | 172.19.8.40 | 255.255.0.0 | 172.19.0.250 | SPARE | DFS 2-AX250-ClF3 | ASD | V15.0.4.111 | V17.0.6.116.5 | 2019-01-17 |  | SHIPPED | 2019-01-17 | 2019-07-01 | _C5 Need new wip
4507362992 | D14204-002 | CO | Carbon Monoxide | B51 Pyro | D14204-002 | 172.19.8.41 | 172.19.8.42 | 255.255.0.0 | 172.19.0.250 | GC5547 | DFS 1-AX250-CO | ASD | V17.0.6.116.5 | V17.0.6.116.5 | 2019-01-17 | 2019-03-19 | SHIPPED | 2019-01-17 | 2023-07-13 | _C5 7/27/23 upd
4507363032 | D14204-003 | COS | Carbonyl Sulfide | B51 Pyro | D14204-003 | 172.19.8.45 | 172.19.8.46 | 255.255.0.0 | 172.19.0.250 | GC5546 | DFS 1-AX250-COS | ASD | V17.0.6.116.5 | V17.0.6.116.5 | 2019-01-17 | 2019-03-19 | SHIPPED | 2019-01-17 | 2023-07-13 | _C5 7/27/23 upd
450450652 | D14251-001 | C2H2 | Acetylene | B24D SF | D14251-001 | 172.19.8.200 | 172.19.8.201 | 255.255.0.0 | 172.19.0.250 | GC9032 | DFS 1-AX250-C2H2 | ASD PIGTAIL PURGE | V15.0.4.115 | V17.0.6.115.1C | 2019-03-25 | 2019-11-18 | SHIPPED | 2019-03-25 | 2021-04-20 | _0B Needs new wip
450450665 | D14251-002 | C2H2 | Acetylene | B24E | D14251-002 | 172.19.8.202 | 172.19.8.203 | 255.255.0.0 | 172.19.0.250 | GC9545 | DFS 1-AX250-C2H2 | ASD PIGTAIL PURGE | V15.0.4.115 | V17.0.6.115.1C | 2019-03-25 | 2020-01-27 | SHIPPED | 2019-03-25 | 2021-04-20 | _0B Needs new wip
450450666 | D14251-003 | C2H2 | Acetylene | B51 Pyro | D14251-003 | 172.19.8.204 | 172.19.8.205 | 255.255.0.0 | 172.19.0.250 | GC5509 | DFS 1-AX250-C2H2 | ASD PIGTAIL PURGE | V17.0.5.115.1C | V17.0.6.115.1C | 2019-03-25 | 2020-11-03 | SHIPPED | 2019-03-25 | 2021-04-20 | _0B 5/11/23 upd
4507450677 | D14251-004 | CH2F2 | Difluoromethane | B51 Pyro | D14251-004 | 172.19.8.50 | 172.19.8.51 | 255.255.0.0 | 172.19.0.250 | GC5544 | DFS 1-AX250-CH2F2 | ASD | V17.0.6.116.5 | V17.0.6.116.5 | 2019-02-01 | 2019-04-29 | SHIPPED | 2019-02-01 | 2023-07-13 | _C5 7/27/23 upd
4507450670 | D14251-005 | CH2F2 | Difluoromethane | B51 Pyro | D14251-005 | 172.19.8.129 | 172.19.8.130 | 255.255.0.0 | 172.19.0.250 | GC5543 | DFS 1-AX250-CH2F2 | ASD | V17.0.6.116.5 | V17.0.6.116.5 | 2019-02-01 | 2019-04-29 | SHIPPED | 2019-02-01 | 2023-07-13 | _C5 7/27/23 upd
4507604001 | D14908-001 | SO2 | Sulfur Dioxide | B51 Oxid | D14908-001 | 172.19.8.206 | 172.19.8.207 | 255.255.0.0 | 172.19.0.250 | GC5311 | DFS 1-AX250-SO2 | ASD | V17.0.6.116.5 | V17.0.6.116.5 | 2019-04-27 | 2019-07-01 | SHIPPED | 2019-04-27 | 2023-09-07 | _C5 upd 9/7/23
4507773884 | D15505-001 | COS | Carbonyl Sulfide | B51 Pyro | D15505-001 | 172.19.8.221 | 172.19.8.222 | 255.255.0.0 | 172.19.0.250 | GC5542 | DFS 1-AX250-COS | ASD | V17.0.6.116.5 | V17.0.6.116.5 | 2019-05-20 | 2019-07-01 | SHIPPED | 2019-05-20 | 2019-07-12 | _C5 7/27/23 upd
4507869388 | D16005-001 | CH3F | Fluoromethane (Halocarbon-41) | B51 Pyro | D16005-001 | 172.19.8.227 | 172.19.8.228 | 255.255.0.0 | 172.19.0.250 | GC5540 | DFS 1-AX250-CH3F | ASD | V17.0.6.116.5 | V17.0.6.116.5 | 2019-06-28 | 2019-10-14 | SHIPPED | 2019-06-28 | 2023-07-13 | _C5 7/27/23 upd
4507869346 | D16005-002 | CH3F | Fluoromethane (Halocarbon-41) | B51 Pyro | D16005-002 | 172.19.8.229 | 172.19.8.230 | 255.255.0.0 | 172.19.0.250 | GC5539 | DFS 1-AX250-CH3F | ASD | V17.0.6.116.5 | V17.0.6.116.5 | 2019-06-28 | 2019-10-14 | SHIPPED | 2019-06-28 | 2023-07-13 | _C5 7/27/23 upd
4507869335 | D16005-003 | D2 | Deuterium | B51 Pyro | D16005-003 | 172.19.8.231 | 172.19.8.232 | 255.255.0.0 | 172.19.0.250 | GC5536 | DFS 1-AX250-D2 | ASD | V17.0.6.116.5 | V17.0.6.116.5 | 2019-09-13 | 2019-10-21 | SHIPPED | 2019-09-13 | 2023-06-30 | _C5 7/27/23 upd
4507869426 | D16005-004 | C3H6 | Propylene | B51 Pyro | D16005-004 | 172.19.8.233 | 172.19.8.234 | 255.255.0.0 | 172.19.0.250 | GC5541 | DFS 1-AX250-C3H6 | ASD | V17.0.6.116.5 | V17.0.6.116.5 | 2019-08-16 | 2019-10-14 | SHIPPED | 2019-08-16 | 2023-07-13 | _C5 7/27/23 upd
4507869399 | D16005-005 | Hartes | Fluorine(<5%) / Nitrogen (HARTES) | B51 Oxid | D16005-005 | 172.19.8.235 | 172.19.8.236 | 255.255.0.0 | 172.19.0.250 | GC5310 | DFS 1-AX250-Hartes | ASD | V17.0.6.116.5 | V17.0.6.116.5 | 2019-08-16 | 2019-10-15 | SHIPPED | 2019-08-16 | 2023-09-07 | _C5 upd 9/7/23
4508152110 | D17003-001 | ClF3 | Chlorine Trifluoride | B51 Oxid | D17003-001 | 172.19.8.243 | 172.19.8.244 | 255.255.0.0 | 172.19.0.250 | GC5309 | DFS 2-AX250-ClF3 | ASD | V15.0.4.111 | V17.0.6.116.5 | 2019-10-23 | 2020-01-31 | SHIPPED | 2019-10-23 | 2019-10-23 | _C5 wip
4508365252 | D17705-001 | C3H6 | Propylene | B51 Pyro | G55B13B14 | 172.19.9.42 | 172.19.9.43 | 255.255.0.0 | 172.19.0.250 | GC5518 | DFS 1-AX250-C3H6 | ASD | V17.0.6.116.5 | V17.0.6.116.5 | 2020-01-03 | 2020-04-22 | SHIPPED | 2020-01-03 | 2023-06-23 | _C5 6/22/23 upd
4508365273 | D17705-002 | C2H6 | Ethane | B51 Pyro | G55D05D06 | 172.19.9.44 | 172.19.9.45 | 255.255.0.0 | 172.19.0.250 | GC5538 | DFS 1-AX250-C2H6 | ASD | V17.0.6.116.5 | V17.0.6.116.5 | 2020-01-14 | 2020-04-22 | SHIPPED | 2020-01-14 | 2023-06-30 | _C5 7/27/23 upd
4508543613 | D18033-001 | GeH4 10%/H2 | Germane(10%) / Hydrogen | B51 Pyro | G55E17E18 | 172.19.9.46 | 172.19.9.47 | 255.255.0.0 | 172.19.0.250 | GC5556 | DFS 1-AX250-GeH4 10%/H2 | ASD | V15.0.4.114 | V17.0.6.116.5 | 2020-04-20 | 2020-08-17 | SHIPPED | 2020-04-20 | 2020-06-18 | _C5 wip upd skipped
4508543615 | D18033-002 | PH3 30%/H2 | Phosphine(30%) / Hydrogen | B51 Pyro | G55E15E16 | 172.19.9.48 | 172.19.9.49 | 255.255.0.0 | 172.19.0.250 | GC5555 | DFS 1-AX250-PH3 30%/H2 | ASD | V17.0.6.116.5 | V17.0.6.116.5 | 2020-04-20 | 2020-08-14 | SHIPPED | 2020-04-20 | 2023-08-10 | _C5 8/10/23 upd
4508543474 | D18033-003 | DCS | Dichlorosilane (DCS) | B51 Pyro | G55E13E14 | 172.19.9.50 | 172.19.9.51 | 255.255.0.0 | 172.19.0.250 | GC5554 | DFS 1-AX250-DCS | ASD | V17.0.6.116.5 | V17.0.6.116.5 | 2020-05-01 | 2020-08-17 | SHIPPED | 2020-05-01 | 2023-08-10 | _C5 8/10/23 upd. Need to update cert
4508541769 | D18033-004 | CH2F2 | Difluoromethane | B51 Pyro | G55D03D04 | 172.19.9.52 | 172.19.9.53 | 255.255.0.0 | 172.19.0.250 | GC5537 | DFS 1-AX250-CH2F2 | ASD | V17.0.6.116.5 | V17.0.6.116.5 | 2020-06-12 | 2020-07-14 | SHIPPED | 2020-06-12 | 2023-06-30 | _C5 7/27/23 upd
4508543652 | D18257-001 | HCl | Hydrogen Chloride | B51 Oxid | G53B03B04 | 172.19.9.54 | 172.19.9.55 | 255.255.0.0 | 172.19.0.250 | GC5320 | DFS 1-AX250-HCl | ASD | V17.0.6.116.5 | V17.0.6.116.5 | 2020-06-14 | 2020-08-18 | SHIPPED | 2020-06-14 | 2023-09-15 | _C5 upd 9/14/23
4508627319 | D18468-001 | Cl2 | Chlorine | B51 Oxid | G53A13A14 | 172.19.9.60 | 172.19.9.61 | 255.255.0.0 | 172.19.0.250 | GC5307 | DFS 1-AX250-Cl2 | ASD | V17.0.6.116.5 | V17.0.6.116.5 | 2020-06-26 | 2021-02-12 | SHIPPED | 2020-06-26 | 2023-09-07 | _C5 upd 9/7/23
4508627293 | D18468-002 | CH4 | Methane | B51 Pyro | G55E11E12 | 172.19.9.62 | 172.19.9.63 | 255.255.0.0 | 172.19.0.250 | GC5553 | DFS 1-AX250-CH4 | ASD | V17.0.6.116.5 | V17.0.6.116.5 | 2020-06-26 | 2020-08-13 | SHIPPED | 2020-06-26 | 2023-08-10 | _C5 8/10/23 upd
4508627378 | D18468-003 | HCl | Hydrogen Chloride | B51 Oxid | G53B01B02 | 172.19.9.64 | 172.19.9.65 | 255.255.0.0 | 172.19.0.250 | GC5319 | DFS 1-AX250-HCl | ASD | V15.0.4.114 | V17.0.6.116.5 | 2020-06-26 | 2020-09-17 | SHIPPED | 2020-06-26 | 2020-06-25 | _C5 wip
4508627350 | D18468-004 | HF | Hydrogen Fluoride | B51 SF | GC57210 | 172.19.9.66 | 172.19.9.67 | 255.255.0.0 | 172.19.0.250 | GC57 210 | DFS 1-AX250-HF | ASD | V15.0.4.114 | V17.0.6.116.5 | 2020-07-07 | 2020-09-28 | SHIPPED | 2020-07-07 | 2020-07-21 | _C5 Need new wip
4508627420 | D18468-005 | HF | Hydrogen Fluoride | B24D SF | GC57217 | 172.19.9.68 | 172.19.9.69 | 255.255.0.0 | 172.19.0.250 | GC9013 | DFS 2-AX250-HF-HEAT | ASD | V15.0.4.114.H | V17.0.6.116.5H | 2020-07-14 | 2021-08-26 | SHIPPED | 2020-07-14 | 2020-08-17 | _F9 Need new wip. First SiCl4,1512,REV114 with 2 zone heat.
4508627415 | D18468-006 | SiH4 | Silane | B51 Pyro | G55E23E24 | 172.19.9.70 | 172.19.9.71 | 255.255.0.0 | 172.19.0.250 | GC5559 | DFS 1-AX250-SiH4 | ASD | V17.0.6.116.5 | V17.0.6.116.5 | 2020-07-21 | 2020-10-05 | SHIPPED | 2020-07-21 | 2023-08-10 | _C5 upd 8/10/23
4508630536 | D18468-007 | C2H2 | Acetylene | B51 Pyro | G55A17A18 | 172.19.9.72 | 172.19.9.73 | 255.255.0.0 | 172.19.0.250 | GC5508 | DFS 1-AX250-C2H2 | ASD PIGTAIL PURGE | V17.0.5.115.1C | V17.0.5.115.1C | 2020-07-28 | 2020-12-15 | SHIPPED | 2020-09-25 | 2021-04-20 | _0B 5/11/23 upd
4508630571 | D18468-008 | C2H2 | Acetylene | B51 Pyro | G55A09A10 | 172.19.9.74 | 172.19.9.75 | 255.255.0.0 | 172.19.0.250 | GC5504 | DFS 1-AX250-C2H2 | ASD PIGTAIL PURGE | V17.0.5.115.1C | V17.0.5.115.1C | 2020-08-05 | 2021-04-08 | SHIPPED | 2020-09-25 | 2021-04-08 | _0B 5/11/23 upd
4508630555 | D18468-009 | C2H2 | Acetylene | B51 Pyro | G55A11A12 | 172.19.9.76 | 172.19.9.77 | 255.255.0.0 | 172.19.0.250 | GC5505 | DFS 1-AX250-C2H2 | ASD PIGTAIL PURGE | V17.0.5.115.1C | V17.0.5.115.1C | 2020-08-05 | 2021-04-08 | SHIPPED | 2020-09-25 | 2021-04-08 | _0B 5/11/23 upd
4508666731 | D18663-001 | TSA | Trisilylamine | B50 SF | GC5010 | 172.19.9.78 | 172.19.9.79 | 255.255.0.0 | 172.19.0.250 | GC5010 | DFS 2-AX250-TSA | ASD | V15.0.4.114 | V17.0.6.116.5 | 2020-08-05 | 2020-09-29 | SHIPPED | 2020-08-10 | 2020-08-10 | _C5 Need new wip
4509261156 | D20127-001 | ClF3 | Chlorine Trifluoride | B51 Oxid | D20127-001 | 172.19.9.118 | 172.19.9.119 | 255.255.0.0 | 172.19.0.250 | GC5306 | DFS 2-AX250-ClF3 | ASD | V15.0.4.115 | V17.0.6.116.5 | 2020-11-14 | 2021-03-05 | SHIPPED | 2020-10-16 | 2021-03-05 | _C5 wip
4509261142 | D20127-002 | PH3 .5%/N2 | Phosphine(0.5%) / Nitrogen | B51 Pyro | D20127-002 | 172.19.9.121 | 172.19.9.122 | 255.255.0.0 | 172.19.0.250 | GC5549 | DFS 1-AX250-PH3 .5%/N2 | ASD | V17.0.6.116.5 | V17.0.6.116.5 | 2020-11-14 | 2021-01-25 | SHIPPED | 2020-10-23 | 2020-10-20 | _C5 7/27/23 upd
4509245324 | D20127-003 | Garnet | GARNET | B51 Pyro | D20127-003 | 172.19.9.125 | 172.19.9.126 | 255.255.0.0 | 172.19.0.250 | GC5550 | DFS 1-AX250-Garnet | ASD | V17.0.6.116.5 | V17.0.6.116.5 | 2020-11-24 | 2020-12-16 | SHIPPED | 2020-11-13 | 2023-08-10 | _C5 8/10/23 upd
4509244545 | D20127-004 | DCS | Dichlorosilane (DCS) | B51 Pyro | D20127-004 | 172.19.9.127 | 172.19.9.128 | 255.255.0.0 | 172.19.0.250 | GC5548 | DFS 1-AX250-DCS | ASD | V17.0.6.116.5 | V17.0.6.116.5 | 2020-11-24 | 2021-02-22 | SHIPPED | 2020-11-13 | 2023-06-23 | _C5 6/22/23 upd
4509244616 | D20127-005 | CH3F | Fluoromethane (Halocarbon-41) | B51 Pyro | D20127-005 | 172.19.9.129 | 172.19.9.130 | 255.255.0.0 | 172.19.0.250 | GC5565 | DFS 1-AX250-CH3F | ASD | V17.0.6.116.5 | V17.0.6.116.5 | 2021-01-11 | 2022-01-17 | SHIPPED | 2021-01-08 | 2023-08-10 | _C5 8/10/23 upd
4509244641 | D20127-006 | H2 | Hydrogen | B51 Pyro | D20127-006 | 172.19.9.131 | 172.19.9.132 | 255.255.0.0 | 172.19.0.250 | GC5564 | DFS 1-AX250-H2 | ASD | V17.0.6.116.5 | V17.0.6.116.5 | 2021-01-13 | 2022-01-17 | SHIPPED | 2021-01-13 | 2023-08-10 | _C5 8/10/23 upd
4509289715 | D20238-001 | WF6 | Tungsten Hexafluoride | B51 SF | D20238-001 | 172.19.9.133 | 172.19.9.134 | 255.255.0.0 | 172.19.0.250 | GC57 200 | DFS 1-AXDPO250-WF6 | ASD | V15.0.4.116 | V17.0.6.116.5 | 2020-12-30 | 2021-03-26 | SHIPPED | 2020-12-30 | 2021-03-29 | _C5 Need new wip
4510571172 | D20621-001 | HF | Hydrogen Fluoride | B51 SF | D20621-001 | 172.19.10.200 | 172.19.10.201 | 255.255.0.0 | 172.19.0.250 | GC57 345 | DFS 1-AXDPO250-HF | ASD | V15.0.4.116.4 | V17.0.6.116.5 | 2022-04-01 |  | SHIPPED | 2022-08-15 | 2022-10-10 | _C5 Need new wip
4510571172 | D20621-002 | HF | Hydrogen Fluoride | B51 SF | D20621-002 | 172.19.10.202 | 172.19.10.203 | 255.255.0.0 | 172.19.0.250 | GC57 201.e21 | DFS 1-AXDPO250-HF-HEAT | ASD | V17.0.6.116.5H | V17.0.6.116.5H | 2022-04-01 |  | SHIPPED | 2022-09-26 | 2023-05-19 | _F9 5/19/23 upd
4510571172 | D20621-003 | F2 20%/N2 | Fluorine(20%) / Nitrogen | B51 Oxid | D20621-003 | 172.19.10.204 | 172.19.10.205 | 255.255.0.0 | 172.19.0.250 | GC5347 | DFS 1-AX250-F2 20%/N2 | ASD | V15.0.4.116.4 | V17.0.6.116.5 | 2022-04-01 | UNK | SHIPPED | 2022-04-25 | 2022-05-26 | _C5 wip
4510571172 | D20621-004 | HF | Hydrogen Fluoride | B51X SF | D20621-004 | 172.19.10.206 | 172.19.10.207 | 255.255.0.0 | 172.19.0.250 | GC57 347 K45 | DFS 1-AXDPO250-HF-HEAT | ASD | V17.0.6.116.5H | V17.0.6.116.5H | 2022-10-28 | 2023-11-27 | SHIPPED | 2022-11-04 | 2022-10-27 | _F9 11/27/23 upd
4510571172 | D20621-005 | F2 20%/N2 | Fluorine(20%) / Nitrogen | B51 Oxid | D20621-005 | 172.19.10.208 | 172.19.10.209 | 255.255.0.0 | 172.19.0.250 | GC5344 | DFS 1-AX250-F2 20%/N2 | ASD | V15.0.4.116.4 | V17.0.6.116.5 | 2022-04-01 | UNK | SHIPPED | 2022-04-25 | 2022-05-26 | _C5 wip
4510571172 | D20621-006 | DCS | Dichlorosilane (DCS) | B51X SF | D20621-006 | 172.19.10.210 | 172.19.10.211 | 255.255.0.0 | 172.19.0.250 | GC57 348 K45 | DFS 1-AXDPO250-DCS-HEAT | ASD | V17.0.6.116.5H | V17.0.6.116.5H | 2022-11-04 | 2023-11-27 | SHIPPED | 2022-11-04 | 2022-10-27 | _F9 11/27/23 upd
4510571172 | D20621-007 | HCl | Hydrogen Chloride | B51 Oxid | D20621-007 | 172.19.10.212 | 172.19.10.213 | 255.255.0.0 | 172.19.0.250 | GC5345 | DFS 1-AX250-HCl | ASD | V15.0.4.116.4 | V17.0.6.116.5 | 2022-04-01 | UNK | SHIPPED | 2022-04-29 | 2022-05-26 | _C5 wip
4510571172 | D20621-008 | NO | Nitric Oxide | B51 Oxid | D20621-008 | 172.19.10.214 | 172.19.10.215 | 255.255.0.0 | 172.19.0.250 | GC5346 | DFS 1-AX250-NO | ASD | V15.0.4.116.4 | V17.0.6.116.5 | 2022-04-01 |  | SHIPPED | 2022-09-22 | 2022-09-22 | _C5 wip
4510571172 | D20621-009 | D2 | Deuterium | B51 Pyro | D20621-009 | 172.19.10.216 | 172.19.10.217 | 255.255.0.0 | 172.19.0.250 | GC5583 | DFS 1-AX250-D2 | ASD | V17.0.6.116.5 | V17.0.6.116.5 | 2022-04-01 |  | SHIPPED | 2022-09-22 | 2023-08-31 | _C5 8/31/23 upd
4510571172 | D20621-010 | C3H6 | Propylene | B51 Pyro | D20621-010 | 172.19.10.218 | 172.19.10.219 | 255.255.0.0 | 172.19.0.250 | GC5582 | DFS 1-AX250-C3H6 | ASD | V17.0.6.116.5 | V17.0.6.116.5 | 2022-04-01 |  | SHIPPED | 2022-09-23 | 2023-08-31 | _C5 8/31/23 upd
4510577782 | D20621-011 | Cactus | Cactus | B51 Pyro | D20621-011 | 172.19.10.220 | 172.19.10.221 | 255.255.0.0 | 172.19.0.250 | GC5558 | DFS 1-AX250-Cactus | ASD | V15.0.4.116.4 | V17.0.6.116.5 | 2022-04-01 | UNK | SHIPPED | 2022-04-25 | 2022-05-26 | _C5 upd 10.12.23 was upgraded from 6B via D21512-005
4510577782 | D20621-012 | ClF3 | Chlorine Trifluoride | B51X | D20621-012 | 172.19.10.222 | 172.19.10.223 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-ClF3-HEAT | ASD | V15.0.4.116.4H | V17.0.6.116.5H | 2022-04-01 |  | SHIPPED | 2022-09-27 | 2022-10-10 | _F9 Need new wip
4510577782 | D20621-013 | PH3 5%/N2 | Phosphine(5%) / Nitrogen | B51 Pyro | D20621-013 | 172.19.10.224 | 172.19.10.225 | 255.255.0.0 | 172.19.0.250 | GC5595 | DFS 1-AX250-PH3 5%/N2 | ASD | V17.0.5.116.5 | V17.0.6.116.5 | 2022-11-08 |  | SHIPPED | 2022-11-08 | 2022-11-14 | _C5 wip upd skipped
4510577782 | D20621-014 | Si2H6 | Disilane | B51 Pyro | D20621-014 | 172.19.10.226 | 172.19.10.227 | 255.255.0.0 | 172.19.0.250 | GC5572 | DFS 1-AX250-Si2H6 | ASD | V17.0.6.116.5 | V17.0.6.116.5 | 2022-11-08 |  | SHIPPED | 2022-11-08 | 2023-08-17 | _C5 8/17/23 upd
4510577782 | D20621-015 | COS | Carbonyl Sulfide | B51 Pyro | D20621-015 | 172.19.10.228 | 172.19.10.229 | 255.255.0.0 | 172.19.0.250 | GC5580 | DFS 1-AX250-COS | ASD | V17.0.6.116.5 | V17.0.6.116.5 | 2022-09-01 |  | SHIPPED | 2022-09-28 | 2023-08-31 | _C5 8/31/23 upd
4510577782 | D20621-016 | HF | Hydrogen Fluoride | B51 Oxid | D20621-016 | 172.19.10.230 | 172.19.10.231 | 255.255.0.0 | 172.19.0.250 | GC5351 | DFS 1-AXDPO250-HF | ASD | V15.0.4.116.4 | V17.0.6.116.5 | 2022-09-01 |  | SHIPPED | 2022-10-04 | 2022-10-10 | _C5 wip
4510577782 | D20621-017 | CL2 | Chlorine | B51 Oxid | D20621-017 | 172.19.10.232 | 172.19.10.233 | 255.255.0.0 | 172.19.0.250 | GC5349 | DFS 1-AX250-CL2 | ASD | V15.0.4.116.4 | V17.0.6.116.5 | 2022-09-01 |  | SHIPPED | 2022-10-04 | 2022-10-10 | _C5 wip
4510577782 | D20621-018 | C4F6 | Hexafluorocyclobutene | B51 Pyro | D20621-018 | 172.19.10.234 | 172.19.10.235 | 255.255.0.0 | 172.19.0.250 | GC5577 | DFS 1-AX250-C4F6 | ASD | V17.0.6.116.5 | V17.0.6.116.5 | 2022-09-01 |  | SHIPPED | 2022-10-06 | 2023-08-31 | _C5 8/31/23 upd
4510577782 | D20621-019 | HBr | Hydrogen Bromide | B51 Oxid | D20621-019 | 172.19.10.236 | 172.19.10.237 | 255.255.0.0 | 172.19.0.250 | GC5350 | DFS 1-AX250-HBr | ASD | V15.0.4.116.4 | V17.0.6.116.5 | 2022-09-01 |  | SHIPPED | 2022-10-06 | 2022-10-14 | _C5 wip
4510577782 | D20621-020 | CH2F2 | Difluoromethane | B51 Pyro | D20621-020 | 172.19.10.238 | 172.19.10.239 | 255.255.0.0 | 172.19.0.250 | GC5578 | DFS 1-AX250-CH2F2 | ASD | V17.0.6.116.5 | V17.0.6.116.5 | 2022-09-01 |  | SHIPPED | 2022-10-10 | 2023-08-31 | _C5 8/31/23 upd
4510577782 | D20621-021 | CH4 | Methane | B51 Pyro | D20621-021 | 172.19.10.240 | 172.19.10.241 | 255.255.0.0 | 172.19.0.250 | GC5576 | DFS 1-AX250-CH4 | ASD | V17.0.6.116.5 | V17.0.6.116.5 | 2022-09-01 |  | SHIPPED | 2022-10-12 | 2023-08-17 | _C5 8/17/23 upd
4510577782 | D20621-022 | SO2 | Sulfur Dioxide | B51 Oxid | D20621-022 | 172.19.10.242 | 172.19.10.243 | 255.255.0.0 | 172.19.0.250 | GC5348 | DFS 1-AX250-SO2 | ASD | V15.0.4.116.4 | V17.0.6.116.5 | 2022-09-01 |  | SHIPPED | 2022-10-17 | 2022-10-14 | _C5 wip
4510577782 | D20621-023 | CH3F | Fluoromethane (Halocarbon-41) | B51 Pyro | D20621-023 | 172.19.10.244 | 172.19.10.245 | 255.255.0.0 | 172.19.0.250 | GC5579 | DFS 1-AX250-CH3F | ASD | V17.0.6.116.5 | V17.0.6.116.5 | 2022-11-04 |  | SHIPPED | 2022-11-04 | 2023-08-31 | _C5 8/31/23 upd
4511034625 | D20621-025 | CO | Carbon Monoxide | B51 Pyro | D20621-025 | 172.19.11.74 | 172.19.11.75 | 255.255.0.0 | 172.19.0.250 | GC5575 | DFS 1-AX250-CO | ASD | V17.0.6.116.5 | V17.0.6.116.5 | 2022-11-14 |  | SHIPPED | 2022-11-18 | 2023-08-17 | _C5 8/17/23 upd
4509545818 | D20747-001 | F2 20%/N2 | Fluorine(20%) / Nitrogen | B51 Oxid | D20747-001 | 172.19.9.153 | 172.19.9.154 | 255.255.0.0 | 172.19.0.250 | GC5304 | DFS 1-AX250-F2 20%/N2 | ASD | V17.0.6.116.5 | V17.0.6.116.5 | 2021-04-01 | 2021-06-21 | SHIPPED | 2021-02-24 | 2023-09-07 | _C5 upd 9/7/23
4509545821 | D20747-002 | HF | Hydrogen Fluoride | B51 SF | D20747-002 | 172.19.9.155 | 172.19.9.156 | 255.255.0.0 | 172.19.0.250 | GC57 212 | DFS 1-AXDPO250-HF | ASD | V15.0.4.116 | V17.0.6.116.5 | 2021-04-01 | 2021-07-21 | SHIPPED | 2021-05-03 | 2021-05-25 | _C5 Need new wip
4509530883 | D20818-001 | HF | Hydrogen Fluoride | B51 SF | D20818-001 | 172.19.9.157 | 172.19.9.158 | 255.255.0.0 | 172.19.0.250 | GC57 211 | DFS 1-AXDPO250-HF-HEAT | ASD | V17.0.5.116.5H | V17.0.5.116.5H | 2021-01-13 | 2021-07-23 | SHIPPED | 2021-06-18 | 2022-01-18 | _F9 need new wip No Cyl Lock code, Update 1/6/23
4509530636 | D20818-002 | PH3 | Phosphine | B51 Pyro | D20818-002 | 172.19.9.190 | 172.19.9.191 | 255.255.0.0 | 172.19.0.250 | GC5570 | DFS 1-AX250-PH3 | ASD | V17.0.6.116.5 | V17.0.6.116.5 | 2021-02-19 | 2021-06-21 | SHIPPED | 2021-05-28 | 2023-08-17 | _C5 8/17/23 upd
4509530672 | D20818-003 | GeH4 10%/H2 | Germane(1%) / Hydrogen | B51 Pyro | D20818-003 | 172.19.9.192 | 172.19.9.193 | 255.255.0.0 | 172.19.0.250 | GC5571 | DFS 1-AX250-GeH4 10%/H2 | ASD | V17.0.6.116.5 | V17.0.6.116.5 | 2021-02-28 | 2021-06-21 | SHIPPED | 2021-05-28 | 2023-08-17 | _C5 8/17/23 upd
4509530693 | D20818-004 | DCS | Dichlorosilane (DCS) | B51 Pyro | D20818-004 | 172.19.9.194 | 172.19.9.195 | 255.255.0.0 | 172.19.0.250 | GC5567 | DFS 1-AX250-DCS | ASD | V17.0.6.116.5 | V17.0.6.116.5 | 2021-02-28 | 2021-06-21 | SHIPPED | 2021-05-28 | 2023-08-17 | _C5 8/17/23 upd
| D20818-005 | CL2 | Chlorine |  |  |  |  | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-CL2 | ASD |  |  |  |  | CANCELED | CANCELED | CANCELED
| D20818-006 | D2 | Deuterium |  |  |  |  | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-D2 | ASD |  |  |  |  | CANCELED | CANCELED | CANCELED
| D20818-007 | Si2H6 | Disilane |  |  |  |  | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-Si2H6 | ASD |  |  |  |  | CANCELED | CANCELED | CANCELED
| D20818-008 | NO | Nitric Oxide |  |  |  |  | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-NO | ASD |  |  |  |  | CANCELED | CANCELED | CANCELED
4509651947 | D20883-001 | HCl | Hydrogen Chloride | B51 Oxid | D20883-001 | 172.19.9.196 | 172.19.9.197 | 255.255.0.0 | 172.19.0.250 | GC5305 | DFS 1-AXDPO250-HCl-HEAT | ASD | V15.0.4.116.2H | V17.0.6.116.5H | 2021-08-13 | 2021-08-19 | SHIPPED | 2021-08-13 | 2021-10-05 | _F9 wip
4509620446 | D21491-001 | B2H6 10%/H2 | Diborane(10%) / Hydrogen | B51 Pyro | D21491-001 | 172.19.9.198 | 172.19.9.199 | 255.255.0.0 | 172.19.0.250 | GC5569 | DFS 1-AX250-B2H6 10%/H2 | ASD | V17.0.6.116.5 | V17.0.6.116.5 | 2021-03-25 | 2021-04-23 | SHIPPED | 2021-04-07 | 2023-08-17 | _C5 8/17/23 upd
4509760469 | D21734-001 | HF | Hydrogen Fluoride | B51 Oxid | D21734-001 | 172.19.9.218 | 172.19.9.219 | 255.255.0.0 | 172.19.0.250 | GC5303 | DFS 1-AXDPO250-HF | ASD | V17.0.6.116.5 | V17.0.6.116.5 | 2021-07-07 | 2021-08-27 | SHIPPED | 2021-07-07 | 2023-09-07 | _C5 upd 9/7/23
4509760615 | D21738-001 | SiCl4 | Silicon Tetrachloride | B50 SF | D21738-001 | 172.19.9.204 | 172.19.9.205 | 255.255.0.0 | 172.19.0.250 | GC5068 | DFS 1-AX250-SiCl4 | ASD | V15.0.4.116 | V17.0.6.116.5 | 2021-07-07 | 2021-07-30 | SHIPPED | 2021-07-07 | 2021-07-30 | _C5 Need new wip
4509761078 | D21747-001 | DCS | Dichlorosilane (DCS) | B50 SF | D21747-001 | 172.19.9.206 | 172.19.9.207 | 255.255.0.0 | 172.19.0.250 | GC5069 | DFS 1-AXDPO250-DCS-HEAT | ASD | V15.0.4.116.H | V17.0.6.116.5H | 2021-07-09 | 2021-07-30 | SHIPPED | 2021-07-09 | 2021-07-30 | _F9 Need new wip
4509761370 | D21748-001 | HF | Hydrogen Fluoride | B24D SF | D21748-001 | 172.19.9.208 | 172.19.9.209 | 255.255.0.0 | 172.19.0.250 | GC9026 | DFS 1-AXDPO250-HF-HEAT | ASD | V15.0.4.116.2H | V17.0.6.116.5H | 2021-08-09 | UNK | SHIPPED | 2021-08-06 | 2021-08-09 | _F9 Need new wip
4509761322 | D21749-001 | DCS | Dichlorosilane (DCS) | B24D SF | D21749-001 | 172.19.9.210 | 172.19.9.211 | 255.255.0.0 | 172.19.0.250 | GC9027 | DFS 1-AXDPO250-DCS-HEAT | ASD | V15.0.4.116.4H | V17.0.6.116.5H | 2021-08-09 | UNK | SHIPPED | 2021-08-06 | 2022-09-26 | _F9 Need new wip
4509852748 | D22100-001 | C4F6 | Hexafluorocyclobutene | B51 Pyro | D22100-001 | 172.19.9.212 | 172.19.9.213 | 255.255.0.0 | 172.19.0.250 | GC5568 | DFS 1-AXDPO250-C4F6 | ASD | V15.0.4.116.2 | V17.0.6.116.5 | 2021-07-30 | 2021-09-20 | SHIPPED | 2021-07-30 | 2021-07-30 | _C5 wip upd skipped
4509878004 | D22101-001 | C4F6 | Hexafluorocyclobutene |  | D22101-001 | 172.19.9.214 | 172.19.9.215 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AXDPO250-C4F6 | ASD |  |  |  |  | CANCELED | CANCELED | CANCELED
4509896197 | D22102-001 | PH3 30%/H2 | Phosphine(30%) / Hydrogen | B51 Pyro | D22102-001 | 172.19.9.216 | 172.19.9.217 | 255.255.0.0 | 172.19.0.250 | GC5566 | DFS 1-AXDPO250-PH3 30%/H2 | ASD | V17.0.6.116.5 | V17.0.6.116.5 | 2021-07-30 | 2021-12-20 | SHIPPED | 2021-07-30 | 2023-08-17 | _C5 8/17/23 upd
4509938326 | D22398-001 | HF | Hydrogen Fluoride | B51 Oxid | D22398-001 | 172.19.9.242 | 172.19.9.243 | 255.255.0.0 | 172.19.0.250 | GC5302 | DFS 1-AX250-HF | ASD | V17.0.6.116.5 | V17.0.6.116.5 | 2021-04-08 | 2021-08-27 | SHIPPED | 2021-08-03 | 2023-09-07 | _C5 upd 9/7/23
| D22476-001 | SiCl4 | Silicon Tetrachloride |  | D22476-001 | 172.19.9.244 | 172.19.9.245 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AXDPO250-SiCl4 | ASD |  |  | 2021-09-01 |  | CANCELED | CANCELED | CANCELED
4509987853 | D22477-001 | SiCl4 | Silicon Tetrachloride | B51 Oxid | D22477-001 | 172.19.9.246 | 172.19.9.247 | 255.255.0.0 | 172.19.0.250 | GC5331 | DFS 1-AXDPO250-SiCl4-HEAT | ASD | V15.0.4.116.4H | V17.0.6.116.5H | 2021-10-29 | 2022-01-20 | SHIPPED | 2021-12-01 | 2021-12-23 | _F9 wip
4510074767 | D22693-001 | HF | Hydrogen Fluoride |  | D22693-001 | 172.19.9.248 | 172.19.9.249 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-HF | ASD |  | V15.0.4.116.4 | 2021-09-15 |  | CANCELED | CANCELED | CANCELED
| D22694-001 | C2H2 | Acetylene |  |  |  |  | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AXDPO250-C2H2 | [5 empty] | CANCELED | CANCELED | CANCELED
4510074839 | D22695-001 | HF | Hydrogen Fluoride | B51 SF | D22695-001 | 172.19.9.250 | 172.19.9.251 | 255.255.0.0 | 172.19.0.250 | GC57 242 | DFS 1-AX250-HF-HEAT | ASD | V15.0.4.116.4H | V17.0.6.116.5H | 2022-02-14 | 2022-05-17 | SHIPPED | 2022-02-25 | 2022-02-24 | _F9 Need new wip.
4510127962 | D22696-001 | HBr | Hydrogen Bromide |  | D22696-001 | 172.19.9.252 | 172.19.9.253 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-HBr | ASD | V15.0.4.115.1 | V17.0.6.116.5 | 2022-02-14 |  | SHIPPED | 2022-02-14 | 2022-05-26 | _C5 Need new wip
4510127665 | D22697-001 | CH3F | Fluoromethane (Halocarbon-41) |  | D22697-001 | 172.19.9.254 | 172.19.9.255 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-CH3F | ASD | V15.0.4.115.1 | V17.0.6.116.5 | 2022-02-14 |  | SHIPPED | 2022-02-14 | 2022-02-22 | _C5 Need new wip
3500784181 | D22701-001 | Jasper | Hydrogen Fluoride | B50 SF | D22701-001 | 172.19.10.6 | 172.19.10.7 | 255.255.0.0 | 172.19.0.250 | GC5067 | DFS 1-AX250-Jasper-HEAT | ASD | V17.0.6.116.5H | V17.0.6.116.5H | 2021-11-08 | 2022-01-15 | SHIPPED | 2021-11-01 | 2023-01-18 | _F9 5/2/23 upd. Need to update cert
4510162425 | D23037-001 | HF | Hydrogen Fluoride | B24D SF | D23037-001 | 172.19.10.8 | 172.19.10.9 | 255.255.0.0 | 172.19.0.250 | GC9028 | DFS 1-AX250-HF-HEAT | ASD | V15.0.4.116.2H | V17.0.6.116.5H | 2021-11-16 | 2022-02-28 | SHIPPED | 2021-12-14 | 2021-12-22 | _F9 Need new wip
4510350762 | D23548-001 | HF | Hydrogen Fluoride | B50 SF | D23548-001 | 172.19.10.27 | 172.19.10.28 | 255.255.0.0 | 172.19.0.250 | GC5060 | DFS 1-AXDPO250-HF | ASD | V15.0.4.116.2 | V17.0.6.116.5 | 2022-10-22 | 2022-02-28 | SHIPPED | 2021-10-20 | 2021-12-22 | _C5 Need new wip
| D23549-001 | DCS | Dichlorosilane (DCS) |  |  |  |  | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AXDPO250-DCS-HEAT | ASD |  | V15.0.4.116.4H |  |  | CANCELED | CANCELED | CANCELED
4510373187 | D23550-001 | EG1 | EG1 | B51 Oxid | D23550-001 | 172.19.10.29 | 172.19.10.30 | 255.255.0.0 | 172.19.0.250 | GC5334 | DFS 1-AXDPO250-EG1 | ASD | V17.0.6.116.5 | V17.0.6.116.5 | 2021-11-01 | 2022-02-28 | SHIPPED | 2021-11-01 | 2021-11-01 | _C5 upd 10/12/23
4510361395 | D23551-001 | HCl | Silicon Tetrachloride | B51 Oxid | D23551-001 | 172.19.10.31 | 172.19.10.32 | 255.255.0.0 | 172.19.0.250 | GC5337 | DFS 1-AXDPO250-HCl-HEAT | ASD | V15.0.4.116.4H | V17.0.6.116.5H | 2022-02-09 | 2022-04-05 | SHIPPED | 2022-02-11 | 2022-07-15 | _F9 wip
4510351314 | D23567-001 | F2 20%/N2 | Fluorine(20%) / Nitrogen |  | D23567-001 | 172.19.10.33 | 172.19.10.34 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AXDPO250-F2 20%/N2 | ASD | V15.0.4.116.2 | V17.0.6.116.5 | 2022-02-21 |  | SHIPPED | 2022-02-21 | 2022-02-22 | _C5 Need new wip
4510360744 | D23569-001 | HF | Hydrogen Fluoride |  | D23569-001 | 172.19.10.35 | 172.19.10.36 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AXDPO250-HF | ASD | V15.0.4.116.4 | V17.0.6.116.5 | 2022-02-28 |  | SHIPPED | 2022-02-28 | 2022-05-26 | _C5 Need new wip
4510361329 | D23606-001 | SiCl4 | Silicon Tetrachloride |  | D23606-001 | 172.19.10.37 | 172.19.10.38 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AXDPO250-SiCl4 | ASD | V15.0.4.116.3 | V17.0.6.116.5 | 2022-02-21 |  | SHIPPED | 2022-02-11 | 2022-02-22 | _C5 Need new wip
4510396066 | D23804-001 | SiCl4 | Silicon Tetrachloride |  | D23804-001 | 172.19.10.39 | 172.19.10.40 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AXDPO250-SiCl4-HEAT | ASD | V15.0.4.116.4H | V17.0.6.116.5H | 2022-03-07 |  | SHIPPED | 2022-03-15 | 2022-05-26 | _F9 Need new wip
4510396115 | D23805-001 | B2H6 .1%/H2 | Diborane(.1%) / Hydrogen | B51 Pyro | D23805-001 | 172.19.10.41 | 172.19.10.42 | 255.255.0.0 | 172.19.0.250 | GC5574 | DFS 1-AX250-B2H6 .1%/H2 | ASD | V17.0.6.116.5 | V17.0.6.116.5 | 2022-03-07 |  | SHIPPED | 2022-03-07 | 2023-08-17 | _C5 8/17/23 upd
4510465047 | D24159-001 | ClF3 | Chlorine Trifluoride | B51 Oxid | D24159-001 | 172.19.10.43 | 172.19.10.44 | 255.255.0.0 | 172.19.0.250 | GC5336 | DFS 1-AX250-ClF3-HEAT | ASD | V15.0.4.116.4H | V17.0.6.116.5H | 2022-03-16 | 2022-03-31 | SHIPPED | 2022-03-22 | 2022-03-24 | _F9 wip
4510478868 | D24160-001 | HF | Hydrogen Fluoride | B51 SF | D24160-001 | 172.19.10.45 | 172.19.10.46 | 255.255.0.0 | 172.19.0.250 | GC57 247 | DFS 1-AXDPO250-HF | ASD | V15.0.4.116.4 | V17.0.6.116.5 | 2022-03-10 | 2022-05-18 | SHIPPED | 2022-03-07 | 2022-03-07 | _C5 Need new wip
4510465133 | D24161-001 | DCS | Dichlorosilane (DCS) | B51 Pyro | D24161-001 | 172.19.10.47 | 172.19.10.48 | 255.255.0.0 | 172.19.0.250 | GC5563 | DFS 1-AX250-DCS-HEAT | ASD | V17.0.6.116.5H | V17.0.6.116.5H | 2022-04-01 | 2022-04-05 | SHIPPED | 2022-03-22 | 2023-08-10 | _F9 8/10/23 upd. Need to update cert
4510464834 | D24162-001 | ClF3 | Chlorine Trifluoride | B51 Oxid | D24162-001 | 172.19.10.49 | 172.19.10.50 | 255.255.0.0 | 172.19.0.250 | GC5335 | DFS 1-AX250-ClF3-HEAT | ASD | V15.0.4.116.4H | V17.0.6.116.5H | 2022-04-07 | 2022-07-27 | SHIPPED | 2022-06-03 | 2022-07-15 | _F9 wip
4510464922 | D24164-001 | HF | Hydrogen Fluoride | B51 Oxid | D24164-001 | 172.19.10.51 | 172.19.10.52 | 255.255.0.0 | 172.19.0.250 | GC5342 | DFS 1-AX250-HF | ASD | V15.0.4.116.4 | V17.0.6.116.5 | 2022-03-22 | 2022-06-09 | SHIPPED | 2022-03-24 | 2022-03-31 | _C5 wip
4510496740 | D24165-001 | C2H2 | Acetylene | B51 Pyro | D24165-001 | 172.19.10.53 | 172.19.10.54 | 255.255.0.0 | 172.19.0.250 | GC5503 | DFS 1-AX250-C2H2 | ASD PIGTAIL PURGE | V17.0.5.115.1C | V17.0.5.115.1C | 2022-04-15 | 2022-12-21 | SHIPPED | 2022-10-30 | 2022-12-21 | _0B 5/11/23 upd
4510478906 | D24166-001 | BCl3 | Boron Trichloride | B51 Oxid | D24166-001 | 172.19.10.55 | 172.19.10.56 | 255.255.0.0 | 172.19.0.250 | GC5341 | DFS 1-AX250-BCl3 | ASD | V15.0.4.116.4 | V17.0.6.116.5 | 2022-03-28 |  | SHIPPED | 2022-03-28 | 2022-03-31 | _C5 wip
4510507836 | D24271-001 | HCl | Hydrogen Chloride | B51 Oxid | D24271-001 | 172.19.10.57 | 172.19.10.58 | 255.255.0.0 | 172.19.0.250 | GC5339 | DFS 1-AXDPO250-HCl-HEAT | ASD | V15.0.4.116.4H | V17.0.6.116.5H | 2022-06-29 | 2022-07-15 | SHIPPED | 2022-04-25 | 2022-07-15 | _F9 wip
4510507857 | D24305-001 | HCl | Hydrogen Chloride | B51 Oxid | D24305-001 | 172.19.10.59 | 172.19.10.60 | 255.255.0.0 | 172.19.0.250 | GC5340 | DFS 1-AXDPO250-HCl-HEAT | ASD | V15.0.4.116.4H | V17.0.6.116.5H | 2022-07-05 | 2022-07-27 | SHIPPED | 2022-05-19 | 2022-07-15 | _F9 wip
4510537337 | D24433-001 | HF | Hydrogen Fluoride | B24D SF | D24433-001 | 172.19.10.246 | 172.19.10.247 | 255.255.0.0 | 172.19.0.250 | GC9021 | DFS 1-AXDPO250-HF-HEAT | ASD | V15.0.4.116.4H | V17.0.6.116.5H | 2022-04-28 | 2022-06-22 | SHIPPED | 2022-04-29 | 2022-06-22 | _F9 Need new wip
4510537344 | D24434-001 | DCS | Dichlorosilane (DCS) | B24D SF | D24434-001 | 172.19.10.248 | 172.19.10.249 | 255.255.0.0 | 172.19.0.250 | GC9022 | DFS 1-AXDPO250-DCS-HEAT | ASD | V15.0.4.116.4H | V17.0.6.116.5H | 2022-04-21 | 2022-06-22 | SHIPPED | 2022-05-04 | 2022-06-22 | _F9 Need new wip
4510548226 | D24436-001 | SiCl4 | Silicon Tetrachloride | B51 Oxid | D24436-001 | 172.19.10.250 | 172.19.10.251 | 255.255.0.0 | 172.19.0.250 | GC5343 | DFS 1-AXDPO250-SiCl4-HEAT | ASD | V15.0.4.116.4H | V17.0.6.116.5H | 2022-05-12 |  | SHIPPED | 2022-07-25 | 2022-07-25 | _F9 wip
4510537893 | D24522-001 | DCS | Dichlorosilane (DCS) | B51 Pyro | D24522-001 | 172.19.10.252 | 172.19.10.253 | 255.255.0.0 | 172.19.0.250 | GC5594 | DFS 1-AXDPO250-DCS-HEAT | ASD | V17.0.6.116.5H | V17.0.6.116.5H | 2022-05-19 |  | SHIPPED | 2022-05-27 | 2023-08-31 | _F9 8/31/23 upd
4510550620 | D24523-001 | CH2F2 | Difluoromethane | B51 Pyro | D24523-001 | 172.19.10.254 | 172.19.10.255 | 255.255.0.0 | 172.19.0.250 | GC5562 | DFS 1-AX250-CH2F2 | ASD | V17.0.6.116.5 | V17.0.6.116.5 | 2022-05-05 |  | SHIPPED | 2022-04-04 | 2023-08-10 | _C5 8/10/23 upd
4510574328 | D24562-001 | HCl | Hydrogen Chloride | B51 Oxid | D24562-001 | 172.19.11.0 | 172.19.11.1 | 255.255.0.0 | 172.19.0.250 | GC5338 | DFS 1-AXDPO250-HCl-HEAT | ASD | V15.0.4.116.4H | V17.0.6.116.5H | 2022-04-11 | 2022-06-15 | SHIPPED | 2022-04-11 | 2022-07-15 | _F9 wip
4510814526 | D24699-001 | PF3 | Phosphorus Trifluoride | B51 Oxid | D24699-001 | 172.19.11.2 | 172.19.11.3 | 255.255.0.0 | 172.19.0.250 | GC5359 | DFS 1-AXDPO250-PF3 | ASD | V17.0.5.116.5 | V17.0.6.116.5 | 2023-01-10 |  | SHIPPED | 2022-12-30 | 2022-12-28 | _C5 5/19/23 upd
4511510958 | D26931-001 | B2H6 10%/H2 | Diborane(10%) / Hydrogen |  | D26931-001 | 172.19.11.60 | 172.19.11.61 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AXDPO250-B2H6 10%/H2-HEAT | ASD | V17.0.5.116.5H | V17.0.6.116.5H | 2022-11-24 |  | SHIPPED | 2022-11-24 | 2022-11-21 | _F9 Need new wip
4511291542 | D27771-001 | B2H6 .1%/H2 | Diborane(.1%) / Hydrogen |  | D27771-001 | 172.19.11.62 | 172.19.11.63 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-B2H6 .1%/H2 | ASD | V17.0.5.116.5 | V17.0.6.116.5 | 2023-01-26 |  | SHIPPED | 2023-02-10 | 2023-03-07 | _C5
4511291542 | D27771-002 | C2H4 | Ethylene | B51 Pyro | D27771-002 | 172.19.11.64 | 172.19.11.65 | 255.255.0.0 | 172.19.0.250 | GC5573 | DFS 1-AX250-C2H4 | ASD | V17.0.6.116.5 | V17.0.6.116.5 | 2023-01-26 |  | SHIPPED | 2022-01-05 | 2023-08-17 | _C5 8/17/23 upd
4511291542 | D27771-003 | CL2 | Chlorine | B51 Oxid | D27771-003 | 172.19.11.66 | 172.19.11.67 | 255.255.0.0 | 172.19.0.250 | GC5353 | DFS 1-AX250-CL2 | ASD | V17.0.5.116.5 | V17.0.6.116.5 | 2023-01-26 |  | SHIPPED | 2023-02-10 | 2023-03-07 | _C5 wip no power
4511291542 | D27771-004 | ClF3 | Chlorine Trifluoride | B51 Oxid | D27771-004 | 172.19.11.68 | 172.19.11.69 | 255.255.0.0 | 172.19.0.250 | GC5355 | DFS 1-AX250-ClF3-HEAT | ASD | V17.0.5.116.5H | V17.0.6.116.5H | 2023-01-26 |  | SHIPPED | 2023-01-26 | 2023-01-31 | _F9 wip
4511291542 | D27771-005 | DCS | Dichlorosilane (DCS) |  | D27771-005 | 172.19.11.70 | 172.19.11.71 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-DCS-HEAT | ASD | V17.0.5.116.5H | V17.0.6.116.5H | 2023-01-26 |  | SHIPPED | 2023-01-26 | 2023-01-31 | _F9 Need new wip
4511291542 | D27771-006 | ClF3 | Chlorine Trifluoride | B51 Oxid | D27771-006 | 172.19.11.72 | 172.19.11.73 | 255.255.0.0 | 172.19.0.250 | GC5354 | DFS 1-AX250-ClF3-HEAT | ASD | V17.0.5.116.5H | V17.0.6.116.5H | 2023-01-26 |  | SHIPPED | 2023-01-26 | 2023-01-31 | _F9 wip no power
4511754901 | D28420-001 | Garnet | GARNET | B51 Pyro | D28420-001 | 172.19.11.152 | 172.19.11.153 | 255.255.0.0 | 172.19.0.250 | GC5592 | DFS 1-AX250-Garnet | ASD | V17.0.6.116.5 | V17.0.6.116.5 | 2023-05-12 |  | SHIPPED | 2023-05-12 | 2023-08-10 | _C5 8/10/23 upd
4511754901 | D28420-002 | C2H2 | Acetylene | B51 Pyro | D28420-002 | 172.19.11.154 | 172.19.11.155 | 255.255.0.0 | 172.19.0.250 | GC5502 | DFS 1-AX250-C2H2 | ASD PIGTAIL PURGE | V17.0.5.115.1C | V17.0.5.115.1C | 2022-11-07 |  | SHIPPED | 2022-12-01 | 2022-12-01 | _0B 5/11/23 upd
4512141882 | D78892-001 | BCl3 | Boron Trichloride |  | D78892-001 | 172.19.11.221 | 172.19.11.222 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-BCl3 | ASD | V17.0.5.116.5 | V17.0.6.116.5 | 2023-04-12 |  | SHIPPED | 2023-04-11 | 2023-04-10 | _C5. update cert
| D78892-002 | C2H4 | Ethylene |  |  |  |  | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-C2H4 | ASD |  | V17.0.5.116.5 |  |  | CANCELED | CANCELED | CANCELED
4512141882 | D78892-003 | C3F6 | Hexafluoropropylene |  | D78892-003 | 172.19.11.223 | 172.19.11.224 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-C3F6-HEAT | ASD |  | V17.0.6.116.5H | 2023-06-23 |  | SHIPPED | 2023-08-08 | 2023-10-16 | _F9 check put/get
4512141639 | D78892-004 | CH2F2 | Difluoromethane |  | D78892-004 | 172.19.11.225 | 172.19.11.226 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-CH2F2 | ASD | V17.0.5.116.5 | V17.0.6.116.5 | 2023-04-07 |  | SHIPPED | 2023-04-07 | 2023-04-10 | _C5. update cert
4512141882 | D78892-005 | C4F6 | Hexafluorocyclobutene |  | D78892-005 | 172.19.11.227 | 172.19.11.228 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-C4F6 | ASD | V17.0.6.116.5 | V17.0.6.116.5 | 2023-06-30 |  | SHIPPED | 2023-07-18 | 2023-07-18 | _C5. Check put/get
4512141882 | D78892-006 | CH3F | Fluoromethane (Halocarbon-41) |  | D78892-006 | 172.19.11.229 | 172.19.11.230 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-CH3F | ASD | V17.0.6.116.5 | V17.0.6.116.5 | 2023-07-07 |  | SHIPPED | 2023-07-18 | 2023-07-18 | _C5. Check put/get
4512141882 | D78892-007 | HBr | Hydrogen Bromide |  | D78892-007 | 172.19.11.231 | 172.19.11.232 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-HBr | ASD | V17.0.6.116.5 | V17.0.6.116.5 | 2023-07-14 |  | SHIPPED | 2023-07-18 | 2023-07-18 | _C5. Check put/get
4512141882 | D78892-008 | SiF4 | Silicon Tetrafluoride |  | D78892-008 | 172.19.11.233 | 172.19.11.234 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-SiF4 | ASD |  | V17.0.6.116.5 | 2023-07-21 |  | SHIPPED | 2023-07-27 | 2023-08-03 | _C5. Check put/get
4512557275 | D88660-001 | C2H2 | Acetylene |  | D88660-001 | 172.19.12.10 | 172.19.12.11 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-C2H2 | ASD PIGTAIL PURGE |  | V17.0.6.115.1C | 2023-12-11 |  | SHIPPED | 2023-12-11 |  | _OB
4512563352 | D88661-001 | HF | Hydrogen Fluoride |  | D88661-001 | 172.19.12.13 | 172.19.12.14 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AXDPO250-HF-HEAT | ASD |  | V17.0.6.116.5H | 2023-12-15 |  | FITUP |  |  | _F9 new ehg errors
4512564957 | D88662-001 | HF | Hydrogen Fluoride |  | D88662-001 | 172.19.12.15 | 172.19.12.16 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AXDPO250-HF-HEAT | ASD |  | V17.0.6.116.5H | 2023-12-19 |  | SHIPPED | 2023-11-01 | 2023-11-14 | _F9
4512565390 | D88664-001 | HF | Hydrogen Fluoride |  | D88664-001 | 172.19.12.17 | 172.19.12.18 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AXDPO250-HF-HEAT | ASD |  | V17.0.6.116.5H | 2023-12-19 |  | FITUP |  |  | _F9 new ehg errors
4512565390 | D88665-001 | HF | Hydrogen Fluoride |  | D88665-001 | 172.19.12.19 | 172.19.12.20 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AXDPO250-HF-HEAT | ASD |  | V17.0.6.116.5H | 2023-12-22 |  | FITUP |  |  | _F9 new ehg errors
4512568138 | D88667-001 | CL2 | Chlorine |  | D88667-001 | 172.19.12.21 | 172.19.12.22 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-CL2 | ASD |  | V17.0.6.116.5 | 2023-12-22 |  | TEST |  |  | _C5
4512568379 | D88668-001 | F2 20%/N2 | Fluorine(20%) / Nitrogen |  | D88668-001 | 172.19.12.23 | 172.19.12.24 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-F2 20%/N2 | ASD |  | V17.0.6.116.5 | 2024-01-08 |  | FITUP |  |  | _C5
4512601091 | D88785-001 | DCS | Dichlorosilane (DCS) |  | D88785-001 | 172.19.12.38 | 172.19.12.39 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-DCS | ASD |  | V17.0.6.116.5 | 2024-01-22 |  |  |  |  | _C5
4512581116 | D88786-001 | HF | Hydrogen Fluoride |  | D88786-001 | 172.19.12.25 | 172.19.12.26 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-HF | ASD |  | V17.0.6.116.5 | 2024-01-15 |  | WIP |  |  | _C5
4512601335 | D88787-001 | CH2CL2 | Dichloromethaneide |  | D88787-001 | 172.19.12.40 | 172.19.12.41 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-CH2CL2 | ASD |  | V17.0.6.116.5 | 2024-01-22 |  |  |  |  | _C5
4512632934 | D88942-001 | WF6 | Tungsten Hexafluoride |  | D88942-001 | 172.19.12.42 | 172.19.12.43 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-WF6 | ASD |  | V17.0.6.116.5 | 2024-03-22 |  |  |  |  | _C5
4512848493 | D89564-001 | HF | Hydrogen Chloride |  | D89564-001 | 172.19.12.205 | 172.19.12.206 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AXDPO250-HF-HEAT | ASD |  | V17.0.6.116.5H | 2024-05-24 |  |  |  |  | _F9
4512918861 | D89564-002 | HF | Hydrogen Fluoride |  | D89564-002 | 172.19.12.207 | 172.19.12.208 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-HF | ASD |  | V17.0.6.116.5 | 2024-02-23 |  |  |  |  | _C5
4512918880 | D89564-003 | HF | Hydrogen Fluoride |  | D89564-003 | 172.19.12.209 | 172.19.12.210 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-HF | ASD |  | V17.0.6.116.5 | 2024-02-23 |  |  |  |  | _C5
4512884895 | D89564-004 | WF6 | Tungsten Hexafluoride |  | D89564-004 | 172.19.12.211 | 172.19.12.212 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-WF6 | ASD |  | V17.0.6.116.5 | 2024-02-16 |  |  |  |  | _C5
| D89564-005 | ClF3 | Chlorine Trifluoride |  |  |  |  | 255.255.0.0 | 172.19.0.250 | [7 empty] | NO PO |  |  | _C5
4512882341 | D89564-007 | HF | Hydrogen Fluoride |  | D89564-007 | 172.19.12.213 | 172.19.12.214 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-HF | ASD |  | V17.0.6.116.5 | 2024-05-24 |  |  |  |  | _C5
4513059151 | D89564-008 | HF | Hydrogen Fluoride |  | D89564-008 | 172.19.12.215 | 172.19.12.216 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AXDPO250-HF-HEAT | ASD |  | V17.0.6.116.5H | 2024-02-16 |  |  |  |  | _F9
4512881901 | D89564-009 | C2H2 | Acetylene |  | D89564-009 | 172.19.12.217 | 172.19.12.218 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-C2H2 | ASD PIGTAIL PURGE |  | V17.0.6.115.1C | 2024-05-20 |  |  |  |  | _OB
4512881901 | D89564-010 | C2H2 | Acetylene |  | D89564-010 | 172.19.12.219 | 172.19.12.220 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-C2H2 | ASD PIGTAIL PURGE |  | V17.0.6.115.1C | 2024-05-20 |  |  |  |  | _OB
4512884727 | D89564-011 | F2 20%/N2 | Fluorine(20%) / Nitrogen |  | D89564-011 | 172.19.12.221 | 172.19.12.222 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-F2 20%/N2 | ASD |  | V17.0.6.116.5 | 2024-02-14 |  |  |  |  | _C5
4513151341 | D89564-012 | C2H4 30%/He | Ethylene(30%) / Helium |  | D89564-012 | 172.19.12.223 | 172.19.12.224 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-C2H4 30%/He | ASD | V17.0.6.116.5 | V17.0.6.116.5 | 2024-05-28 |  |  |  |  | _C5
4512882297 | D89564-013 | SiCl4 | Silicon Tetrachloride |  | D89564-013 | 172.19.12.225 | 172.19.12.226 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-SiCl4 | ASD |  | V17.0.6.116.5 | 2024-02-14 |  |  |  |  | _C5
| D89564-014 | HF | Hydrogen Fluoride |  |  |  |  | 255.255.0.0 | 172.19.0.250 | [7 empty] | NO PO |  |  | _F9
4512848493 | D89564-015 | HCL | Hydrogen Chloride | [7 empty] | DFS 1-AX250-HCL | ASD |  | V17.0.6.116.5 | 2024-04-26 |  |  |  |  | _C5
4512969240 | D90258-001 | HF | Hydrogen Fluoride |  | D90258-001 | 172.19.12.227 | 172.19.12.228 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AXDPO250-HF-HEAT | ASD |  | V17.0.6.116.5H | 2024-05-22 |  |  |  |  | _F9
4513027733 | D90259-001 | HF | Hydrogen Fluoride |  | D90259-001 | 172.19.12.229 | 172.19.12.230 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AXDPO250-HF-HEAT | ASD |  | V17.0.6.116.5H | 2024-05-22 |  |  |  |  | _F9
4513127477 | D90750-001 | DCS | Dichlorosilane (DCS) |  | D90750-001 | 172.19.12.231 | 172.19.12.232 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-DCS | ASD |  | V17.0.6.116.5 | 2024-05-28 |  |  |  |  | _C5
4513127494 | D90751-001 | DCS | Dichlorosilane (DCS) |  | D90751-001 | 172.19.12.233 | 172.19.12.234 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-DCS | ASD |  | V17.0.6.116.5 | 2024-05-30 |  |  |  |  | _C5
4513221753 | D91021-001 | WF6 | Tungsten Hexafluoride |  | D91021-001 | 172.19.12.235 | 172.19.12.236 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-WF6 | ASD |  | V17.0.6.116.5 | [5 empty] | _C5
4513194651 | D91022-001 | HF | Hydrogen Fluoride |  | D91022-001 | 172.19.12.237 | 172.19.12.238 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AXDPO250-HF-HEAT | ASD |  | V17.0.6.116.5H | [5 empty] | _F9
4513193563 | D91023-001 | HF | Hydrogen Fluoride |  | D91023-001 | 172.19.12.239 | 172.19.12.240 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AXDPO250-HF-HEAT | ASD |  | V17.0.6.116.5H | [5 empty] | _F9
4513227736 | D91024-001 | C2H4 | Ethylene |  | D91024-001 | 172.19.12.241 | 172.19.12.242 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-C2H4 | ASD |  | V17.0.6.116.5 | [5 empty] | _C5
4513190277 | D91025-001 | HF | Hydrogen Fluoride |  | D91025-001 | 172.19.12.243 | 172.19.12.244 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AXDPO250-HF | ASD |  | V17.0.6.116.5 | [5 empty] | _C5
4513184503 | D91026-001 | HBr | Hydrogen Bromide |  | D91026-001 | 172.19.12.245 | 172.19.12.246 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-HBr | ASD |  | V17.0.6.116.5 | [5 empty] | _C5
[8 empty] | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250- | ASD
[8 empty] | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250- | ASD
[8 empty] | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250- | ASD
Note on P1: Requested Date
Note on R1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Project Status CANCELED=Customer Cancelled KO = Kick Off WIP=Work In Progress SHIPPED=Shipped
Note on S1: Actual date

## MTI VMB
PO | PROJECT | GAS | GAS NAME | BLDG | PLC HOSTNAME | PLC IP | HMI IP | Subnet Mask | Gateway | GC# | MODEL | PROGRAM | INSTALLED VER | WIP VER | DELIVERY | COMMISSIONED | STATUS | SHIPPED | ProgSent | Notes
4508899287 | D17279 | 2NTE |  | B51 SF | D17279-001 | 172.19.9.142 | 172.19.9.143 | 255.255.0.0 | 172.19.0.250 | LX574102 | DFS 8-AX250-2NTE | LVMB | V16.0.3.0 | V16.0.6.2 | 2020-12-18 |  | SHIPPED | 2020-12-30 | 2020-12-30
4508965605 | D19498 | 2NTE |  | B51 SF | D19498-001 | 172.19.9.144 | 172.19.9.145 | 255.255.0.0 | 172.19.0.250 | LX574104 | DFS 8-AX250-2NTE | LVMB | V16.0.3.0 | V16.0.6.2 | 2020-12-18 |  | SHIPPED | 2020-12-30 | 2020-12-30
4510051769 | D22691 | 2NTE |  | B51 SF | D22691 | 172.19.10.10 | 172.19.10.11 | 255.255.0.0 | 172.19.0.250 | LX574103 | DFS 8-AX250-2NTE | LVMB | V16.0.5.2 | V16.0.6.2 | 2021-12-29 |  | SHIPPED | 2021-11-22 | 2022-02-11 | UPD 2/11/22
4510051798 | D22692 | 2NTE |  | B50 SF | D22692 | 172.19.10.12 | 172.19.10.13 | 255.255.0.0 | 172.19.0.250 | LX501103 | DFS 8-AX250-2NTE | LVMB | V16.0.5.2 | V16.0.6.2 | 2021-12-29 |  | SHIPPED | 2021-11-22 | 2022-02-11 | UPD 2/11/22
4510087292 | D21706-001 | TOPAZ | Methanol(MEOH) | B51 SF | D21706 | 172.19.10.19 | 172.19.10.20 | 255.255.0.0 | 172.19.0.250 | LX573301 | DFS 8-AX250-TOPAZ | VAPVMB | V17.0.5.1 | V17.0.6.1 | 2022-02-01 | 2022-07-28 | SHIPPED | 2022-01-28 | 2022-07-18 | _10
4510464959 | D24163-001 | TOPAZ | Methanol(MEOH) | B50 SF | D24163-001 | 172.19.10.61 | 172.19.10.62 | 255.255.0.0 | 172.19.0.250 | LX500601/J7 | DFS 8-AX250-TOPAZ | VAPVMB | V17.0.5.1 | V17.0.6.1 | 2022-05-23 |  | SHIPPED | 2022-05-23 | 2022-08-25 | _10
4510824969 | D24700-001 | TOPAZ | Methanol(MEOH) | B51 SF | D24700-001 | 172.19.10.196 | 172.19.10.197 | 255.255.0.0 | 172.19.0.250 | LX573302 | DFS 8-AX250-TOPAZ | VAPVMB | V16.0.6.1 | V17.0.6.1 | 2022-10-19 |  | SHIPPED | 2022-08-30 | 2022-10-18 | _10
4512221834 | D28402-001 | TOPAZ | Methanol(MEOH) |  | D28402-001 | 172.19.11.217 | 172.19.11.218 |  |  |  | DFS 8-AX250-TOPAZ | VAPVMB | V17.0.6.1 | V17.0.6.1 | 2023-09-05 |  | TEST |  |  | _10
4510869331 | D25582-001 | 2NTE |  | B51X SF | D25582-001 | 172.19.10.198 | 172.19.10.199 | 255.255.0.0 | 172.19.0.250 | LX577301 K43 | DFS 8-AX250-2NTE | LVMB | V17.0.6.3 | V17.0.6.3 | 2023-04-28 |  | SHIPPED | 2023-08-14 | 2023-11-27 | _5 11/27/23 upd
4511034705 | D25859-001 | 2NTE |  | B51 SF | D25859-001 | 172.19.11.150 | 172.19.11.151 | 255.255.0.0 | 172.19.0.250 | LX575501 | DFS 8-AX250-2NTE | LVMB | V17.0.5.2 | V17.0.5.2 | 2023-03-28 |  | SHIPPED | 2023-03-28 |  | _5
4512164068 | D28403-001 | 2NTE |  |  | D28403-001 | 172.19.11.219 | 172.19.11.220 |  |  |  | DFS 8-AX250-2NTE | LVMB |  | V17.0.6.3 | 2023-11-13 |  | TEST |  |  | _5
Note on P1: Requested Date
Note on R1: QUOTED DESIGN LOADED SHIPPED
Note on S1: Actual date

## MTI LDC
PO | PROJECT | LIQUID | PLC HOSTNAME | HMI HOSTNAME | PLC IP | HMI IP | Subnet Mask | Gateway | GC# | MODEL | PROGRAM | INSTALLED VER | WIP VER | DELIVERY | COMMISSIONED | STATUS | SHIPPED | ProgSent | Notes
4510857864 | D24279-001 | SiCl4 | D24279-001 | HMI-D24279-001 | 172.19.11.238 | 172.19.11.239 | 255.255.0.0 | 172.19.0.250 |  | DFS 4_AX250_SiCl4 | LDC |  |  | 2023-04-19 |  | LOADED | 2023-06-13 |  | 05112023 14:45 ¦ AJB: D number branch created and loaded into system.
4510857864 | D24279-002 | TCS | D24279-002 | HMI-D24279-002 | 172.19.11.240 | 172.19.11.241 | 255.255.0.0 | 172.19.0.250 |  | DFS 4_AX250_TCS | LDC |  |  | 2023-05-03 |  | LOADED | 2023-06-13 |  | 05112023 14:45 ¦ AJB: D number branch created and loaded into system.
4510901767 | D24279-003 | TOPAZ | D24279-003 | HMI-D24279-003 | 172.19.11.242 | 172.19.11.243 | 255.255.0.0 | 172.19.0.250 |  | DFS 4_AX250_TOPAZ | LDC |  |  | 2023-05-17 |  | LOADED | 2023-06-19 |  | 06162023 15:11 ¦ AJB: Branch created and system loaded with most recent DEV
4510901767 | D24279-004 | 2NTE | D24279-004 | HMI-D24279-004 | 172.19.11.244 | 172.19.11.245 | 255.255.0.0 | 172.19.0.250 |  | DFS 4_AX250_2NTE | LDC |  |  | 2023-05-31 |  | LOADED | 2023-06-19 |  | 06162023 15:40 ¦ AJB: Branch created and system loaded with most recent DEV
4511400256 | D26332-001 | TCS | D26332-001 | HMI-D26332-001 | 172.19.11.246 | 172.19.11.247 | 255.255.0.0 | 172.19.0.250 |  | DFS 4_AX250_TCS | LDC |  |  | 2023-03-30 |  | LOADED | 4/25/2023
4511400256 | D26332-002 | TCS | D26332-002 | HMI-D26332-002 | 172.19.11.248 | 172.19.11.249 | 255.255.0.0 | 172.19.0.250 |  | DFS 4_AX250_TCS | LDC |  |  | 2023-04-05 |  | LOADED | 4/25/2023
4512568633 | D78603-001 | SiCl4 | D78603-001 | HMI-D78603-001 | 172.19.12.0 | 172.19.12.1 | 255.255.0.0 | 172.19.0.250 |  | DFS 4_AX250_SiCl4 | LDC |  |  | 2024-03-08
4512578289 | D88784-001 | TiCl4 | D88784-001 | HMI-D88784-001 | 172.19.12.8 | 172.19.12.9 | 255.255.0.0 | 172.19.0.250 |  | DFS 4_AX250_TiCl4 | LDC |  |  | 2024-03-01
4512882341 | D89564-006 | Si-C | D89564-006 | HMI_D89564-006 | 172.19.12.193 | 172.19.12.194 | 255.255.0.0 | 172.19.0.250 |  | DFS 4_AX250_Si-C |  |  |  | 2024-04-22
4512939207 | D90011-001 | P41 | D90011-001 | HMI_D90011-001 | 172.19.12.195 | 172.19.12.196 | 255.255.0.0 | 172.19.0.250 |  | DFS 4_AX250_P41 |  |  |  | 2024-04-15
4512938562 | D90012-001 | 2NTe | D90012-001 | HMI_D90012-001 | 172.19.12.197 | 172.19.12.198 | 255.255.0.0 | 172.19.0.250 |  | DFS 4_AX250_2NTe |  |  |  | 2024-04-22
4513018423 | D90257-001 | SELATINE | D90257-001 | HMI_D90257-001 | 172.19.12.199 | 172.19.12.200 | 255.255.0.0 | 172.19.0.250 |  | DFS 4_AX250_SELATINE |  |  |  | 2024-05-02
4513120093 | D90622-001 | TMSDMA | D90622-001 | HMI_D90622-001 | 172.19.12.201 | 172.19.12.202 | 255.255.0.0 | 172.19.0.250 |  | DFS 4_AX250_TMSDMA |  |  |  | 2024-03-26
4513059151 | D90663-001 | RENA | D90663-001 | HMI_D90663-001 | 172.19.12.203 | 172.19.12.204 | 255.255.0.0 | 172.19.0.250 |  | DFS 4_AX250_RENA |  |  |  | 2024-05-13
4513194473 | D91027-001 | ENKI LDS04 | D91027-001 | HMI_D91027-001 | 172.19.12.245 | 172.19.12.246 | 255.255.0.0 | 172.19.0.250 |  | DFS 4_AX250_ENKI LDS04 |  |  |  | 2024-04-26
|  |  | 0 | HMI_ | [5 empty] | DFS 4_AX250_
|  |  | 0 | HMI_ | [5 empty] | DFS 4_AX250_
|  |  | 0 | HMI_ | [5 empty] | DFS 4_AX250_
|  |  | 0 | HMI_ | [5 empty] | DFS 4_AX250_
|  |  | 0 | HMI_ | [5 empty] | DFS 4_AX250_
Note on O1: Requested Date
Note on Q1: QUOTED DESIGN LOADED SHIPPED
Note on R1: Actual date

## MTI FLX
PO | PROJECT | GAS | GAS NAME | BLDG | PLC HOSTNAME | PLC IP | HMI IP | Subnet Mask | Gateway | GP | MODEL | PROGRAM | INSTALLED VER | WIP VER | DELIVERY | COMMISSIONED | STATUS | SHIPPED | ProgSent | Notes
3500593347 | D19860-001 | CLF3 | Chlorine Trifluoride | B24E | D19860-001 | 172.19.0.162 | 172.19.0.163 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-CLF3 | AcvFLX | V16.0.4.0 | V16.0.4.0 | 2021-02-15 |  | SHIPPED | 2018-01-01
3500602114 | D19860-002 | TBD | Silane |  | D19860-002 | 172.19.9.161 | 172.19.9.162 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-TBD | AcvFLX | V17.0.5.1 | V17.0.5.1 | 2021-02-15 |  | SHIPPED | 2021-03-19 | 2021-03-29 | upd 12/30/22
3500602114 | D19860-003 | TBD | Silane |  | D19860-003 | 172.19.9.163 | 172.19.9.164 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-TBD | AcvFLX | V17.0.5.1 | V17.0.5.1 | 2021-02-15 |  | SHIPPED | 2021-03-26 | 2021-04-02 | upd 12/29/22
3500602114 | D19860-004 | TBD | Silane |  | D19860-004 | 172.19.9.165 | 172.19.9.166 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-TBD | AcvFLX | V17.0.5.1 | V17.0.5.1 | 2021-02-15 |  | SHIPPED | 2021-05-18 | 2021-04-08 | upd gasname 12/30/22.
3500602114 | D19860-005 | TBD | Silane |  | D19860-005 | 172.19.9.167 | 172.19.9.168 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-TBD | AcvFLX | V17.0.5.1 | V17.0.5.1 | 2021-02-15 |  | SHIPPED | 2021-05-18 | 2021-05-25 | upd 12/29/22
3500602114 | D19860-006 | TBD | Silane |  | D19860-006 | 172.19.9.169 | 172.19.9.170 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-TBD | AcvFLX | V17.0.5.1 | V17.0.5.1 | 2021-02-15 |  | SHIPPED | 2021-05-25 | 2021-05-25 | upd 12/29/22
3500602114 | D19860-007 | TBD | Silane |  | D19860-007 | 172.19.9.171 | 172.19.9.172 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-TBD | AcvFLX | V17.0.5.1 | V17.0.5.1 | 2021-02-15 |  | SHIPPED | 2021-05-25 | 2021-05-25 | upd 12/29/22
3500602114 | D19860-008 | TBD | Silane |  | D19860-008 | 172.19.9.173 | 172.19.9.174 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-TBD | AcvFLX | V17.0.5.1 | V17.0.5.1 | 2021-02-15 |  | SHIPPED | 2021-05-18 | 2021-05-25 | upd 12/29/22
3500602114 | D19860-009 | TBD | Silane |  | D19860-009 | 172.19.9.175 | 172.19.9.176 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-TBD | AcvFLX | V17.0.5.1 | V17.0.5.1 | 2021-02-15 |  | SHIPPED | 2021-05-19 | 2021-05-25 | upd 12/29/22
3500602114 | D19860-010 | TBD | Silane |  | D19860-010 | 172.19.9.177 | 172.19.9.178 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-TBD | AcvFLX | V17.0.5.1 | V17.0.5.1 | 2021-02-15 |  | SHIPPED | 2021-05-19 | 2021-05-25 | upd 12/29/22
3500602114 | D19860-011 | HE | Silane | B51 Inert | D19860-011 | 172.19.9.184 | 172.19.9.185 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-HE | AcvFLX | V17.0.5.1 | V17.0.5.1 | 2021-02-15 |  | SHIPPED | 2021-06-03 | 2022-12-21 | upd 12/21/22
3500602114 | D19860-012 | TBD | Silane |  | D19860-012 | 172.19.9.187 | 172.19.9.188 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-TBD | AcvFLX | V16.0.4.0 | V16.0.4.0 | 2021-02-15 |  | SHIPPED | 2021-06-03 | 2022-03-24
4510464697 | D23109-001 | TBD |  |  | D23109-001 | 172.19.10.63 | 172.19.10.64 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-TBD | AcvFLX | V16.0.5.1 | V16.0.5.1 | 2021-12-14 |  | SHIPPED | 2022-03-28 | 2022-07-06
4510464697 | D23109-002 | TBD |  |  | D23109-002 | 172.19.10.65 | 172.19.10.66 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-TBD | AcvFLX | V16.0.5.1 | V16.0.5.1 | 2021-12-14 |  | SHIPPED | 2022-03-28 | 2022-07-06
4510464697 | D23109-003 | TBD |  |  | D23109-003 | 172.19.10.67 | 172.19.10.68 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-TBD | AcvFLX | V16.0.5.1 | V16.0.5.1 | 2021-12-14 |  | SHIPPED | 2022-03-28 | 2022-07-06
4510464697 | D23109-004 | TBD |  |  | D23109-004 | 172.19.10.69 | 172.19.10.70 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-TBD | AcvFLX | V16.0.5.1 | V16.0.5.1 | 2021-12-14 |  | SHIPPED | 2022-03-28 | 2022-07-06
4510464697 | D23109-005 | TBD |  |  | D23109-005 | 172.19.10.71 | 172.19.10.72 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-TBD | AcvFLX | V16.0.5.1 | V16.0.5.1 | 2021-12-14 |  | SHIPPED | 2022-03-28 | 2022-07-06
4510464697 | D23109-006 | TBD |  |  | D23109-006 | 172.19.10.73 | 172.19.10.74 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-TBD | AcvFLX | V16.0.5.1 | V16.0.5.1 | 2021-12-14 |  | SHIPPED | 2022-03-28 | 2022-07-06
4510464697 | D23109-007 | TBD |  |  | D23109-007 | 172.19.10.75 | 172.19.10.76 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-TBD | AcvFLX | V16.0.5.1 | V16.0.5.1 | 2021-12-14 |  | SHIPPED | 2022-03-28 | 2022-07-06
4510464697 | D23109-008 | TBD |  |  | D23109-008 | 172.19.10.77 | 172.19.10.78 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-TBD | AcvFLX | V16.0.5.1 | V16.0.5.1 | 2021-12-14 |  | SHIPPED | 2022-03-28 | 2022-07-06
4510464697 | D23109-009 | TBD |  |  | D23109-009 | 172.19.10.79 | 172.19.10.80 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-TBD | AcvFLX | V16.0.5.1 | V16.0.5.1 | 2021-12-14 |  | SHIPPED | 2022-03-28 | 2022-07-06
4510464697 | D23109-010 | TBD |  |  | D23109-010 | 172.19.10.81 | 172.19.10.82 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-TBD | AcvFLX | V16.0.5.1 | V16.0.5.1 | 2021-12-14 |  | SHIPPED | 2022-03-28 | 2022-07-06
4510464697 | D23109-011 | TBD |  |  | D23109-011 | 172.19.10.83 | 172.19.10.84 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-TBD | AcvFLX | V17.0.5.1 | V17.0.5.1 | 2021-12-14 |  | SHIPPED | 2022-05-27 | 2022-07-06 | upd 12/30/22
4510464697 | D23109-012 | TBD |  |  | D23109-012 | 172.19.10.85 | 172.19.10.86 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-TBD | AcvFLX | V17.0.5.1 | V17.0.5.1 | 2021-12-14 |  | SHIPPED | 2022-05-27 | 2022-07-06 | upd 12/30/22
4510464697 | D23109-013 | BCL3/N2 |  | B51 Inert | D23109-013 | 172.19.10.87 | 172.19.10.88 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-BCL3/N2 | AcvFLX | V17.0.5.1 | V17.0.5.1 | 2021-12-14 |  | SHIPPED | 2022-05-27 | 2022-12-21 | upd 12/21/22
4510464697 | D23109-014 | HE |  | B51 SF | D23109-014 | 172.19.10.89 | 172.19.10.90 | 255.255.0.0 | 172.19.0.250 | GP57 404 | DFS 1-AX250-HE | AcvFLX | V16.0.5.1 | V16.0.5.1 | 2021-12-14 |  | SHIPPED | 2022-05-27 | 2022-07-06
4510464697 | D23109-015 | TBD |  |  | D23109-015 | 172.19.10.91 | 172.19.10.92 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-TBD | AcvFLX | V17.0.5.1 | V17.0.5.1 | 2021-12-14 |  | SHIPPED | 2022-05-27 | 2022-07-06 | upd gasname 12/30/22
4510464697 | D23109-016 | HE |  | B51 Inert | D23109-016 | 172.19.10.93 | 172.19.10.94 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-HE | AcvFLX | V17.0.5.1 | V17.0.5.1 | 2021-12-14 |  | SHIPPED | 2022-05-27 | 2022-12-21 | upd 12/21/22
4510464697 | D23109-017 | TBD |  |  | D23109-017 | 172.19.10.95 | 172.19.10.96 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-TBD | AcvFLX | V17.0.5.1 | V17.0.5.1 | 2021-12-14 |  | SHIPPED | 2022-05-27 | 2022-07-06 | upd 12/30/22
4510464697 | D23109-018 | TBD |  |  | D23109-018 | 172.19.10.97 | 172.19.10.98 | 255.255.0.0 | 172.19.0.250 | GC4509 | DFS 1-AX250-TBD | AcvFLX | V17.0.5.1 | V17.0.5.1 | 2021-12-14 |  | SHIPPED | 2022-05-27 | 2022-07-06 | upd 12/30/22
4510464697 | D23109-019 | TBD |  |  | D23109-019 | 172.19.10.99 | 172.19.10.100 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-TBD | AcvFLX | V17.0.5.1 | V17.0.5.1 | 2021-12-14 |  | SHIPPED | 2022-05-27 | 2022-07-06 | upd gasname 12/30/22. bad rear ethernet port
4510464697 | D23109-020 | TBD |  |  | D23109-020 | 172.19.10.101 | 172.19.10.102 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-TBD | AcvFLX | V17.0.5.1 | V17.0.5.1 | 2021-12-14 |  | SHIPPED | 2022-05-27 | 2022-07-06 | upd gasname 12/30/22
4510464697 | D23109-021 | TBD |  |  | D23109-021 | 172.19.10.103 | 172.19.10.104 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-TBD | AcvFLX | V16.0.6.1 | V16.0.6.1 | 2022-07-25 |  | SHIPPED | 2022-07-19 | 2022-07-06
4510464697 | D23109-022 | TBD |  |  | D23109-022 | 172.19.10.105 | 172.19.10.106 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-TBD | AcvFLX | V16.0.6.1 | V16.0.6.1 | 2022-07-25 |  | SHIPPED | 2022-07-19 | 2022-07-06
4510464697 | D23109-023 | TBD |  |  | D23109-023 | 172.19.10.107 | 172.19.10.108 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-TBD | AcvFLX | V16.0.6.1 | V16.0.6.1 | 2022-07-25 |  | SHIPPED | 2022-07-19 | 2022-07-06
4510464697 | D23109-024 | TBD |  |  | D23109-024 | 172.19.10.109 | 172.19.10.110 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-TBD | AcvFLX | V16.0.6.1 | V16.0.6.1 | 2022-07-25 |  | SHIPPED | 2022-07-19 | 2022-07-06
4510464697 | D23109-025 | TBD |  |  | D23109-025 | 172.19.10.111 | 172.19.10.112 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-TBD | AcvFLX | V16.0.6.1 | V16.0.6.1 | 2022-07-25 |  | SHIPPED | 2022-07-19 | 2022-07-06
4510464697 | D23109-026 | TBD |  |  | D23109-026 | 172.19.10.113 | 172.19.10.114 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-TBD | AcvFLX | V16.0.6.1 | V16.0.6.1 | 2022-07-25 |  | SHIPPED | 2022-07-19 | 2022-07-06
4510464697 | D23109-027 | TBD |  |  | D23109-027 | 172.19.10.115 | 172.19.10.116 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-TBD | AcvFLX | V16.0.6.1 | V16.0.6.1 | 2022-07-25 |  | SHIPPED | 2022-07-19 | 2022-07-06
4510464697 | D23109-028 | TBD |  |  | D23109-028 | 172.19.10.117 | 172.19.10.118 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-TBD | AcvFLX | V16.0.6.1 | V16.0.6.1 | 2022-07-25 |  | SHIPPED | 2022-07-19 | 2022-07-06
4510464697 | D23109-029 | TBD |  |  | D23109-029 | 172.19.10.119 | 172.19.10.120 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-TBD | AcvFLX | V16.0.6.1 | V16.0.6.1 | 2022-07-25 |  | SHIPPED | 2022-07-19 | 2022-07-06
4510464697 | D23109-030 | TBD |  |  | D23109-030 | 172.19.10.121 | 172.19.10.122 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-TBD | AcvFLX | V16.0.6.1 | V16.0.6.1 | 2022-07-25 |  | SHIPPED | 2022-07-19 | 2022-07-06
4510464697 | D23109-031 | TBD |  |  | D23109-031 | 172.19.10.123 | 172.19.10.124 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-TBD | AcvFLX | V16.0.6.1 | V16.0.6.1 | 2022-07-25 |  | SHIPPED | 2022-07-19 | 2022-07-06
4510464697 | D23109-032 | TBD |  |  | D23109-032 | 172.19.10.125 | 172.19.10.126 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-TBD | AcvFLX | V16.0.6.1 | V16.0.6.1 | 2022-08-15 |  | SHIPPED | 2022-08-26 | 2022-07-06
4510464697 | D23109-033 | TBD |  |  | D23109-033 | 172.19.10.127 | 172.19.10.128 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-TBD | AcvFLX | V16.0.6.1 | V16.0.6.1 | 2022-08-15 |  | SHIPPED | 2022-08-26 | 2022-07-06
4510464697 | D23109-034 | TBD |  |  | D23109-034 | 172.19.10.129 | 172.19.10.130 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-TBD | AcvFLX | V16.0.6.1 | V16.0.6.1 | 2022-08-15 |  | SHIPPED | 2022-08-26 | 2022-07-06
4510464697 | D23109-035 | TBD |  |  | D23109-035 | 172.19.10.131 | 172.19.10.132 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-TBD | AcvFLX | V16.0.6.1 | V16.0.6.1 | 2022-08-15 |  | SHIPPED | 2022-08-26 | 2022-07-06
4510464697 | D23109-036 | TBD |  |  | D23109-036 | 172.19.10.133 | 172.19.10.134 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-TBD | AcvFLX | V16.0.6.1 | V16.0.6.1 | 2022-08-15 |  | SHIPPED | 2022-08-26 | 2022-07-06
4510464697 | D23109-037 | TBD |  |  | D23109-037 | 172.19.10.135 | 172.19.10.136 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-TBD | AcvFLX | V16.0.6.1 | V16.0.6.1 | 2022-08-15 |  | SHIPPED | 2022-08-26 | 2022-07-06
4510464697 | D23109-038 | TBD |  |  | D23109-038 | 172.19.10.137 | 172.19.10.138 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-TBD | AcvFLX | V16.0.6.1 | V16.0.6.1 | 2022-08-15 |  | SHIPPED | 2022-08-26 | 2022-07-06
4510464697 | D23109-039 | TBD |  |  | D23109-039 | 172.19.10.139 | 172.19.10.140 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-TBD | AcvFLX | V16.0.6.1 | V16.0.6.1 | 2022-08-15 |  | SHIPPED | 2022-08-26 | 2022-07-06
4510464697 | D23109-040 | TBD |  |  | D23109-040 | 172.19.10.141 | 172.19.10.142 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-TBD | AcvFLX | V16.0.6.1 | V16.0.6.1 | 2022-08-15 |  | SHIPPED | 2022-08-26 | 2022-07-06
4510464697 | D23109-041 | TBD |  |  | D23109-041 | 172.19.10.143 | 172.19.10.144 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-TBD | AcvFLX | V16.0.6.1 | V16.0.6.1 | 2022-08-15 |  | SHIPPED | 2022-08-26 | 2022-09-22
4510464697 | D23109-042 | TBD |  |  | D23109-042 | 172.19.10.145 | 172.19.10.146 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-TBD | AcvFLX | V16.0.6.1 | V16.0.6.1 | 2022-09-12 |  | SHIPPED | 2022-09-12 | 2022-09-22
4510464697 | D23109-043 | TBD |  |  | D23109-043 | 172.19.10.147 | 172.19.10.148 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-TBD | AcvFLX | V16.0.6.1 | V16.0.6.1 | 2022-09-12 |  | SHIPPED | 2022-09-12 | 2022-09-22
4510464697 | D23109-044 | TBD |  |  | D23109-044 | 172.19.10.149 | 172.19.10.150 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-TBD | AcvFLX | V16.0.6.1 | V16.0.6.1 | 2022-09-12 |  | SHIPPED | 2022-09-12 | 2022-09-22
4510464697 | D23109-045 | TBD |  |  | D23109-045 | 172.19.10.151 | 172.19.10.152 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-TBD | AcvFLX | V16.0.6.1 | V16.0.6.1 | 2022-09-12 |  | SHIPPED | 2022-09-12 | 2022-09-22
4510464697 | D23109-046 | TBD |  |  | D23109-046 | 172.19.10.153 | 172.19.10.154 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-TBD | AcvFLX | V16.0.6.1 | V16.0.6.1 | 2022-09-12 |  | SHIPPED | 2022-09-28 | 2022-09-22
4510464697 | D23109-047 | TBD |  |  | D23109-047 | 172.19.10.155 | 172.19.10.156 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-TBD | AcvFLX | V16.0.6.1 | V16.0.6.1 | 2022-09-12 |  | SHIPPED | 2022-09-28 | 2022-09-22
4510464697 | D23109-048 | TBD |  |  | D23109-048 | 172.19.10.157 | 172.19.10.158 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-TBD | AcvFLX | V16.0.6.1 | V16.0.6.1 | 2022-09-12 |  | SHIPPED | 2022-09-28 | 2022-09-22
4510464697 | D23109-049 | TBD |  |  | D23109-049 | 172.19.10.159 | 172.19.10.160 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-TBD | AcvFLX | V16.0.6.1 | V16.0.6.1 | 2022-09-12 |  | SHIPPED | 2022-09-28 | 2022-09-22
4510464697 | D23109-050 | TBD |  |  | D23109-050 | 172.19.10.161 | 172.19.10.162 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-TBD | AcvFLX | V16.0.6.1 | V16.0.6.1 | 2022-09-12 |  | SHIPPED | 2022-09-28 | 2022-09-22
4510464697 | D23109-051 | TBD |  |  | D23109-051 | 172.19.10.163 | 172.19.10.164 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-TBD | AcvFLX | V16.0.6.1 | V16.0.6.1 | 2022-09-12 |  | SHIPPED | 2022-09-28 | 2022-09-22
3500762152 | D25007-001 | TBD |  |  | D25007-001 |  |  | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-TBD | AcvFLX |  |  | 2021-12-30 |  | CANCELED
4511921052 | D86127-001 | TBD |  |  | D86127-001 | 172.19.11.110 | 172.19.11.111 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-TBD | AcvFLX | V17.0.5.1 | V17.0.5.1 | 2023-01-01 |  | SHIPPED | 2022-12-28
4511921052 | D86127-002 | TBD |  |  | D86127-002 | 172.19.11.112 | 172.19.11.113 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-TBD | AcvFLX | V17.0.5.1 | V17.0.5.1 | 2023-01-01 |  | SHIPPED | 2022-12-28
4511921052 | D86127-003 | TBD |  |  | D86127-003 | 172.19.11.114 | 172.19.11.115 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-TBD | AcvFLX | V17.0.5.1 | V17.0.5.1 | 2023-01-01 |  | SHIPPED | 2022-12-28
4511921052 | D86127-004 | TBD |  |  | D86127-004 | 172.19.11.116 | 172.19.11.117 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-TBD | AcvFLX | V17.0.5.1 | V17.0.5.1 | 2023-01-01 |  | SHIPPED | 2022-12-28
4511921052 | D86127-005 | TBD |  |  | D86127-005 | 172.19.11.118 | 172.19.11.119 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-TBD | AcvFLX | V17.0.5.1 | V17.0.5.1 | 2023-01-01 |  | SHIPPED | 2022-12-28
4511921052 | D86127-006 | TBD |  |  | D86127-006 | 172.19.11.120 | 172.19.11.121 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-TBD | AcvFLX | V17.0.5.1 | V17.0.5.1 | 2023-01-01 |  | SHIPPED | 2022-12-28
4511921052 | D86127-007 | TBD |  |  | D86127-007 | 172.19.11.122 | 172.19.11.123 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-TBD | AcvFLX | V17.0.5.1 | V17.0.5.1 | 2023-01-01 |  | SHIPPED | 2022-12-28
4511921052 | D86127-008 | TBD |  |  | D86127-008 | 172.19.11.124 | 172.19.11.125 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-TBD | AcvFLX | V17.0.5.1 | V17.0.5.1 | 2023-01-01 |  | SHIPPED | 2022-12-28
4511921052 | D86127-009 | TBD |  |  | D86127-009 | 172.19.11.126 | 172.19.11.127 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-TBD | AcvFLX | V17.0.5.1 | V17.0.5.1 | 2023-01-01 |  | SHIPPED | 2022-12-28
4511921052 | D86127-010 | TBD |  |  | D86127-010 | 172.19.11.128 | 172.19.11.129 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-TBD | AcvFLX | V17.0.5.1 | V17.0.5.1 | 2023-01-01 |  | SHIPPED | 2022-12-28
4511921052 | D86127-011 | TBD |  |  | D86127-011 | 172.19.11.130 | 172.19.11.131 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-TBD | AcvFLX | V17.0.5.1 | V17.0.5.1 | 2023-01-01 |  | SHIPPED | 2022-12-28
4511921052 | D86127-012 | TBD |  |  | D86127-012 | 172.19.11.132 | 172.19.11.133 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-TBD | AcvFLX | V17.0.5.1 | V17.0.5.1 | 2023-01-01 |  | SHIPPED | 2022-12-28
4511921052 | D86127-013 | TBD |  |  | D86127-013 | 172.19.11.134 | 172.19.11.135 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-TBD | AcvFLX | V17.0.5.1 | V17.0.5.1 | 2023-01-01 |  | SHIPPED | 2022-12-28
4511921052 | D86127-014 | TBD |  |  | D86127-014 | 172.19.11.136 | 172.19.11.137 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-TBD | AcvFLX | V17.0.5.1 | V17.0.5.1 | 2023-01-01 |  | SHIPPED | 2022-12-28
4511921052 | D86127-015 | TBD |  |  | D86127-015 | 172.19.11.138 | 172.19.11.139 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-TBD | AcvFLX | V17.0.5.1 | V17.0.5.1 | 2023-01-01 |  | SHIPPED | 2022-12-28
4511921052 | D86127-016 | TBD |  |  | D86127-016 | 172.19.11.140 | 172.19.11.141 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-TBD | AcvFLX | V17.0.5.1 | V17.0.5.1 | 2023-01-01 |  | SHIPPED | 2022-12-28
4511921052 | D86127-017 | TBD |  |  | D86127-017 | 172.19.11.142 | 172.19.11.143 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-TBD | AcvFLX | V17.0.5.1 | V17.0.5.1 | 2023-01-01 |  | SHIPPED | 2022-12-28
4511921052 | D86127-018 | TBD |  |  | D86127-018 | 172.19.11.144 | 172.19.11.145 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-TBD | AcvFLX | V17.0.5.1 | V17.0.5.1 | 2023-01-01 |  | SHIPPED | 2022-12-28
4511921052 | D86127-019 | TBD |  |  | D86127-019 | 172.19.11.146 | 172.19.11.147 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-TBD | AcvFLX | V17.0.5.1 | V17.0.5.1 | 2023-01-01 |  | SHIPPED | 2022-12-28
4511921052 | D86127-020 | TBD |  |  | D86127-020 | 172.19.11.148 | 172.19.11.149 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-AX250-TBD | AcvFLX | V17.0.5.1 | V17.0.5.1 | 2023-01-01 |  | SHIPPED | 2022-12-28
[8 empty] | 255.255.0.0 | 172.19.0.250
[8 empty] | 255.255.0.0 | 172.19.0.250
[8 empty] | 255.255.0.0 | 172.19.0.250
[8 empty] | 255.255.0.0 | 172.19.0.250
[8 empty] | 255.255.0.0 | 172.19.0.250
[8 empty] | 255.255.0.0 | 172.19.0.250
[8 empty] | 255.255.0.0 | 172.19.0.250
[8 empty] | 255.255.0.0 | 172.19.0.250
[8 empty] | 255.255.0.0 | 172.19.0.250
[8 empty] | 255.255.0.0 | 172.19.0.250
[8 empty] | 255.255.0.0 | 172.19.0.250
[8 empty] | 255.255.0.0 | 172.19.0.250
[8 empty] | 255.255.0.0 | 172.19.0.250
[8 empty] | 255.255.0.0 | 172.19.0.250
[8 empty] | 255.255.0.0 | 172.19.0.250
[8 empty] | 255.255.0.0 | 172.19.0.250
[8 empty] | 255.255.0.0 | 172.19.0.250
[8 empty] | 255.255.0.0 | 172.19.0.250
[8 empty] | 255.255.0.0 | 172.19.0.250
[8 empty] | 255.255.0.0 | 172.19.0.250
[8 empty] | 255.255.0.0 | 172.19.0.250
[8 empty] | 255.255.0.0 | 172.19.0.250
[8 empty] | 255.255.0.0 | 172.19.0.250
[8 empty] | 255.255.0.0 | 172.19.0.250
[8 empty] | 255.255.0.0 | 172.19.0.250
[8 empty] | 255.255.0.0 | 172.19.0.250
[8 empty] | 255.255.0.0 | 172.19.0.250
[8 empty] | 255.255.0.0 | 172.19.0.250
[8 empty] | 255.255.0.0 | 172.19.0.250
[8 empty] | 255.255.0.0 | 172.19.0.250
[8 empty] | 255.255.0.0 | 172.19.0.250
[8 empty] | 255.255.0.0 | 172.19.0.250
[8 empty] | 255.255.0.0 | 172.19.0.250
[8 empty] | 255.255.0.0 | 172.19.0.250
[8 empty] | 255.255.0.0 | 172.19.0.250
[8 empty] | 255.255.0.0 | 172.19.0.250
[8 empty] | 255.255.0.0 | 172.19.0.250
[8 empty] | 255.255.0.0 | 172.19.0.250
[8 empty] | 255.255.0.0 | 172.19.0.250
[8 empty] | 255.255.0.0 | 172.19.0.250
[8 empty] | 255.255.0.0 | 172.19.0.250
[8 empty] | 255.255.0.0 | 172.19.0.250
[8 empty] | 255.255.0.0 | 172.19.0.250
[8 empty] | 255.255.0.0 | 172.19.0.250
[8 empty] | 255.255.0.0 | 172.19.0.250
[8 empty] | 255.255.0.0 | 172.19.0.250
[8 empty] | 255.255.0.0 | 172.19.0.250
[8 empty] | 255.255.0.0 | 172.19.0.250
[8 empty] | 255.255.0.0 | 172.19.0.250
[8 empty] | 255.255.0.0 | 172.19.0.250
[8 empty] | 255.255.0.0 | 172.19.0.250
[8 empty] | 255.255.0.0 | 172.19.0.250
[8 empty] | 255.255.0.0 | 172.19.0.250
[8 empty] | 255.255.0.0 | 172.19.0.250
[8 empty] | 255.255.0.0 | 172.19.0.250
[8 empty] | 255.255.0.0 | 172.19.0.250
[8 empty] | 255.255.0.0 | 172.19.0.250
[8 empty] | 255.255.0.0 | 172.19.0.250
[8 empty] | 255.255.0.0 | 172.19.0.250
Note on P1: Requested Date
Note on R1: QUOTED DESIGN LOADED SHIPPED
Note on S1: Actual date

## MTI VMB FLX
PO | PROJECT | GAS | GAS NAME | BLDG | PLC HOSTNAME | PLC IP | HMI IP | Subnet Mask | Gateway | MODEL | PROGRAM | INSTALLED VER | WIP VER | DELIVERY | COMMISSIONED | STATUS | SHIPPED | ProgSent | Notes
3501009727 | D87348-001 | TBD |  | B51X |  | 172.19.12.44 | 172.19.12.45 | 255.255.0.0 | 172.19.0.250 | DFS 8-AX250-TBD |  |  |  | 2023-12-15 |  | Loaded
3501009727 | D87348-002 | TBD |  | B51X |  | 172.19.12.46 | 172.19.12.47 | 255.255.0.0 | 172.19.0.250 | DFS 8-AX250-TBD |  |  |  | 2023-12-15 |  | Loaded
3501009727 | D87348-003 | TBD |  | B51X |  | 172.19.12.48 | 172.19.12.49 | 255.255.0.0 | 172.19.0.250 | DFS 8-AX250-TBD |  |  |  | 2023-12-15 |  | KO
3501009727 | D87348-004 | TBD |  | B51X |  | 172.19.12.50 | 172.19.12.51 | 255.255.0.0 | 172.19.0.250 | DFS 8-AX250-TBD |  |  |  | 2023-12-15 |  | KO
3501009727 | D87348-005 | TBD |  | B51X |  | 172.19.12.52 | 172.19.12.53 | 255.255.0.0 | 172.19.0.250 | DFS 8-AX250-TBD |  |  |  | 2023-12-15 |  | KO
3501009727 | D87348-006 | TBD |  | B51X |  | 172.19.12.54 | 172.19.12.55 | 255.255.0.0 | 172.19.0.250 | DFS 8-AX250-TBD |  |  |  | 2023-12-15 |  | KO
3501009727 | D87348-007 | TBD |  | B51X |  | 172.19.12.56 | 172.19.12.57 | 255.255.0.0 | 172.19.0.250 | DFS 8-AX250-TBD |  |  |  | 2023-12-15 |  | KO
3501009727 | D87348-008 | TBD |  | B51X |  | 172.19.12.58 | 172.19.12.59 | 255.255.0.0 | 172.19.0.250 | DFS 8-AX250-TBD |  |  |  | 2023-12-15 |  | KO
3501009727 | D87348-009 | TBD |  | B51X |  | 172.19.12.60 | 172.19.12.61 | 255.255.0.0 | 172.19.0.250 | DFS 8-AX250-TBD |  |  |  | 2023-12-15 |  | KO
3501009727 | D87348-010 | TBD |  | B51X |  | 172.19.12.62 | 172.19.12.63 | 255.255.0.0 | 172.19.0.250 | DFS 8-AX250-TBD |  |  |  | 2023-12-15 |  | KO
3501009727 | D87348-011 | TBD |  | B51X |  | 172.19.12.64 | 172.19.12.65 | 255.255.0.0 | 172.19.0.250 | DFS 8-AX250-TBD |  |  |  | 2023-12-15 |  | KO
3501009727 | D87348-012 | TBD |  | B51X |  | 172.19.12.66 | 172.19.12.67 | 255.255.0.0 | 172.19.0.250 | DFS 8-AX250-TBD |  |  |  | 2023-12-15 |  | KO
3501009727 | D87348-013 | TBD |  | B51X |  | 172.19.12.68 | 172.19.12.69 | 255.255.0.0 | 172.19.0.250 | DFS 8-AX250-TBD |  |  |  | 2023-12-15 |  | KO
3501009727 | D87348-014 | TBD |  | B51X |  | 172.19.12.70 | 172.19.12.71 | 255.255.0.0 | 172.19.0.250 | DFS 8-AX250-TBD |  |  |  | 2023-12-15 |  | KO
3501009727 | D87348-015 | TBD |  | B51X |  | 172.19.12.72 | 172.19.12.73 | 255.255.0.0 | 172.19.0.250 | DFS 8-AX250-TBD |  |  |  | 2023-12-15 |  | KO
3501009726 | D87348-016 | TBD |  | B51X |  | 172.19.12.74 | 172.19.12.75 | 255.255.0.0 | 172.19.0.250 | DFS 8-AX250-TBD |  |  |  | 2023-12-15 |  | KO
3501009726 | D87348-017 | TBD |  | B51X |  | 172.19.12.76 | 172.19.12.77 | 255.255.0.0 | 172.19.0.250 | DFS 8-AX250-TBD |  |  |  | 2023-12-15 |  | KO
3501009726 | D87348-018 | TBD |  | B51X |  | 172.19.12.78 | 172.19.12.79 | 255.255.0.0 | 172.19.0.250 | DFS 8-AX250-TBD |  |  |  | 2023-12-15 |  | KO
3501009726 | D87348-019 | TBD |  | B51X |  | 172.19.12.80 | 172.19.12.81 | 255.255.0.0 | 172.19.0.250 | DFS 8-AX250-TBD |  |  |  | 2023-12-15 |  | KO
3501009726 | D87348-020 | TBD |  | B51X |  | 172.19.12.82 | 172.19.12.83 | 255.255.0.0 | 172.19.0.250 | DFS 8-AX250-TBD |  |  |  | 2023-12-15 |  | KO
3501012909 | D87348-021 | TBD |  | B51X |  | 172.19.12.84 | 172.19.12.85 | 255.255.0.0 | 172.19.0.250 | DFS 8-AX250-TBD |  |  |  | 2023-12-15 |  | KO
3501012909 | D87348-022 | TBD |  | B51X |  | 172.19.12.86 | 172.19.12.87 | 255.255.0.0 | 172.19.0.250 | DFS 8-AX250-TBD |  |  |  | 2023-12-15 |  | KO
3501012909 | D87348-023 | TBD |  | B51X |  | 172.19.12.88 | 172.19.12.89 | 255.255.0.0 | 172.19.0.250 | DFS 8-AX250-TBD |  |  |  | 2023-12-15 |  | Loaded
3501012909 | D87348-024 | TBD |  | B51X |  | 172.19.12.90 | 172.19.12.91 | 255.255.0.0 | 172.19.0.250 | DFS 8-AX250-TBD |  |  |  | 2023-12-15 |  | KO
3501012909 | D87348-025 | TBD |  | B51X |  | 172.19.12.92 | 172.19.12.93 | 255.255.0.0 | 172.19.0.250 | DFS 8-AX250-TBD |  |  |  | 2023-12-15 |  | KO
3501012909 | D87348-026 | TBD |  | B51X |  | 172.19.12.94 | 172.19.12.95 | 255.255.0.0 | 172.19.0.250 | DFS 8-AX250-TBD |  |  |  | 2023-12-15 |  | KO
3501012909 | D87348-027 | TBD |  | B51X |  | 172.19.12.96 | 172.19.12.97 | 255.255.0.0 | 172.19.0.250 | DFS 8-AX250-TBD |  |  |  | 2023-12-15 |  | KO
3501012909 | D87348-028 | TBD |  | B51X |  | 172.19.12.98 | 172.19.12.99 | 255.255.0.0 | 172.19.0.250 | DFS 8-AX250-TBD |  |  |  | 2023-12-15 |  | KO
3501012909 | D87348-029 | TBD |  | B51X |  | 172.19.12.100 | 172.19.12.101 | 255.255.0.0 | 172.19.0.250 | DFS 8-AX250-TBD |  |  |  | 2023-12-15 |  | KO
3501012909 | D87348-030 | TBD |  | B51X |  | 172.19.12.102 | 172.19.12.103 | 255.255.0.0 | 172.19.0.250 | DFS 8-AX250-TBD |  |  |  | 2023-12-15 |  | KO
3501012909 | D87348-031 | TBD |  | B51X |  | 172.19.12.104 | 172.19.12.105 | 255.255.0.0 | 172.19.0.250 | DFS 8-AX250-TBD |  |  |  | 2023-12-15 |  | KO
3501012909 | D87348-032 | TBD |  | B51X |  | 172.19.12.106 | 172.19.12.107 | 255.255.0.0 | 172.19.0.250 | DFS 8-AX250-TBD |  |  |  | 2023-12-15 |  | KO
3501015132 | D87348-033 | TBD |  | B51X |  | 172.19.12.108 | 172.19.12.109 | 255.255.0.0 | 172.19.0.250 | DFS 8-AX250-TBD |  |  |  | 2023-12-15 |  | KO
3501015132 | D87348-034 | TBD |  | B51X |  | 172.19.12.110 | 172.19.12.111 | 255.255.0.0 | 172.19.0.250 | DFS 8-AX250-TBD |  |  |  | 2023-12-15 |  | KO
3501015132 | D87348-035 | TBD |  | B51X |  | 172.19.12.112 | 172.19.12.113 | 255.255.0.0 | 172.19.0.250 | DFS 8-AX250-TBD |  |  |  | 2023-12-15 |  | KO
3501015132 | D87348-036 | TBD |  | B51X |  | 172.19.12.114 | 172.19.12.115 | 255.255.0.0 | 172.19.0.250 | DFS 8-AX250-TBD |  |  |  | 2023-12-15 |  | KO
3501015132 | D87348-037 | TBD |  | B51X |  | 172.19.12.116 | 172.19.12.117 | 255.255.0.0 | 172.19.0.250 | DFS 8-AX250-TBD |  |  |  | 2023-12-15 |  | KO
3501015132 | D87348-038 | TBD |  | B51X |  | 172.19.12.118 | 172.19.12.119 | 255.255.0.0 | 172.19.0.250 | DFS 8-AX250-TBD |  |  |  | 2023-12-15 |  | KO
3501015132 | D87348-039 | TBD |  | B51X |  | 172.19.12.120 | 172.19.12.121 | 255.255.0.0 | 172.19.0.250 | DFS 8-AX250-TBD |  |  |  | 2023-12-15 |  | KO
3501015132 | D87348-040 | TBD |  | B51X |  | 172.19.12.122 | 172.19.12.123 | 255.255.0.0 | 172.19.0.250 | DFS 8-AX250-TBD |  |  |  | 2023-12-15 |  | KO
3501015132 | D87348-041 | TBD |  | B51X |  | 172.19.12.124 | 172.19.12.125 | 255.255.0.0 | 172.19.0.250 | DFS 8-AX250-TBD |  |  |  | 2023-12-15 |  | KO
3501015132 | D87348-042 | TBD |  | B51X |  | 172.19.12.126 | 172.19.12.127 | 255.255.0.0 | 172.19.0.250 | DFS 8-AX250-TBD |  |  |  | 2023-12-15 |  | KO
3501015132 | D87348-043 | TBD |  | B51X |  | 172.19.12.128 | 172.19.12.129 | 255.255.0.0 | 172.19.0.250 | DFS 8-AX250-TBD |  |  |  | 2023-12-15 |  | KO
3501015132 | D87348-044 | TBD |  | B51X |  | 172.19.12.130 | 172.19.12.131 | 255.255.0.0 | 172.19.0.250 | DFS 8-AX250-TBD |  |  |  | 2023-12-15 |  | KO
Note on O1: Requested Date
Note on Q1: QUOTED DESIGN LOADED SHIPPED
Note on R1: Actual date

## MTS VMB
PO | PROJECT | GAS | GAS NAME | BLDG | PLC HOSTNAME | LOCATION | PLC IP | HMI IP | Subnet Mask | Gateway | GC# | MODEL | PROGRAM | INSTALLED VER | WIP VER | DELIVERY | COMMISSIONED | STATUS | SHIPPED | ProgSent | Notes
81036404 | D26233-001 | NF3 |  | F10A2 | D17279-001 | F36U | 10.195.123.23 | 10.195.123.65 | 255.255.252.0 | 10.195.120.1 |  | DFS 8-AX250-NF3 | VMB |  | V17.0.4.0 | 2022-09-22 |  | WIP
81036404 | D26233-002 | NF3 |  |  | D19498-001 | F39V | 10.195.123.22 | 10.195.123.64 | 255.255.252.0 | 10.195.120.1 |  | DFS 8-AX250-NF3 | VMB |  | V17.0.6.0 | 2023-04-20 |  | WIP
Note on Q1: Requested Date
Note on S1: QUOTED DESIGN LOADED SHIPPED
Note on T1: Actual date

## MTV
PO | PROJECT | GAS | GAS NAME | BLDG | PLC HOSTNAME | PLC IP | HMI IP | Subnet Mask | Gateway | GC# | MODEL | PROGRAM | INSTALLED VER | WIP VER | DELIVERY | COMMISSIONED | STATUS | ProgSent | Notes
DEMO |  | WF6 | [8 empty] | DFS 1-AX250-WF6 | DEEP PURGE ASD |  | V15.0.1.AD110 |  |  | QUOTE
NONE | D11792-001 | HF | [8 empty] | DFS 2-AX250-HF-H | STANDARD ASD+HEAT |  | V15.0.1.DSH110 |  |  | QUOTE
NONE | D11792-002 | HF VMB | [8 empty] | DFS 1-AX250-HF VMB | [5 empty] | QUOTE
NONE | D11792-003 | PH3 50ppm | [8 empty] | DFS 1-AX250-PH3 50ppm | STANDARD ASD |  | V15.0.1.AS110 |  |  | QUOTE
NONE | D11792-004 | PH3 500ppm | [8 empty] | DFS 1-AX250-PH3 500ppm | STANDARD ASD |  | V15.0.1.AS110 |  |  | QUOTE
NONE | D11792-005 | PH3 500ppmVMB | [8 empty] | DFS 1-AX250-PH3 500ppmVMB | [5 empty] | QUOTE
NONE | D11792-006 | PH3 1% | [8 empty] | DFS 1-AX250-PH3 1% | STANDARD ASD |  | V15.0.1.AS110 |  |  | QUOTE
NONE | D11792-007 | PH3 1%VMB | [8 empty] | DFS 1-AX250-PH3 1%VMB | [5 empty] | QUOTE
NONE | D11792-008 | PH3 5% | [8 empty] | DFS 1-AX250-PH3 5% | STANDARD ASD |  | V15.0.1.AS110 |  |  | QUOTE
NONE | D11792-009 | PH3 5%VMB | [8 empty] | DFS 1-AX250-PH3 5%VMB | [5 empty] | QUOTE
NONE | D11792-010 | GeH4/H2 10% | [8 empty] | DFS 1-AX250-GeH4/H2 10% | STANDARD ASD |  | V15.0.1.AS110 |  |  | QUOTE
NONE | D11792-011 | TSA | [8 empty] | DFS 1-AX250-TSA | STANDARD ASD |  | V15.0.1.AS110 |  |  | QUOTE
NONE | D11792-012 | CH4 | [8 empty] | DFS 1-AX250-CH4 | STANDARD ASD |  | V15.0.1.AS110 |  |  | QUOTE
NONE | D11792-013 | CH4 VMB | [8 empty] | DFS 1-AX250-CH4 VMB | [5 empty] | QUOTE
NONE | D11792-014 | CH4 2.7% | [8 empty] | DFS 1-AX250-CH4 2.7% | STANDARD ASD |  | V15.0.1.AS110 |  |  | QUOTE
NONE | D11792-015 | CH4 2.7%VMB | [8 empty] | DFS 1-AX250-CH4 2.7%VMB | [5 empty] | QUOTE
NONE | D11792-016 | COS | [8 empty] | DFS 1-AX250-COS | STANDARD ASD |  | V15.0.1.AS110 |  |  | QUOTE
NONE | D11792-017 | CF31 | [8 empty] | DFS 1-AX250-CF31 | STANDARD ASD |  | V15.0.1.AS110 |  |  | QUOTE
NONE | D11792-018 | N20(BSGS) | [8 empty] | DFS 1-AX250-N20(BSGS) | STANDARD ASD |  | V15.0.1.AS110 |  |  | QUOTE
NONE | D11792-019 | N20(BSGS) | [8 empty] | DFS 1-AX250-N20(BSGS) | STANDARD ASD |  | V15.0.1.AS110 |  |  | QUOTE
3500379570 | D15846-001 | C2H2 | Acetylene |  | na | 10.110.28.164 | 10.110.28.134 | 255.255.252.0 | 10.110.31.254 |  | DFS 1-AX250-C2H2 | PIGTAIL PURGE ASD | V15.0.4.113 | V15.0.4.113 | 2019-11-13 | 2019-02-20 | shipped
| D23548-001 | HF | [12 empty] | 2021-10-22
| D23567-001 | F2 20% N2 | [12 empty] | 2022-02-04
| D23569-001 | HF | [12 empty] | 2022-02-10
| D23606-001 | SiCl4 | [12 empty] | 2022-02-04

## Intel MGC
PO | PROJECT | GAS | GAS NAME | BLDG | PLC HOSTNAME | PLC IP | HMI IP | Subnet Mask | Gateway | GC# | MODEL | PROGRAM | INSTALLED VER | WIP VER | DELIVERY | COMMISSIONED | STATUS | Site | Notes
NONE | D18327 | NF3 | Nitrogen Trifluoride | TBD | NA | 172.19.8.57 | 172.19.8.58 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-250-NF3 | STANDARD+HEAT | V16.0.5.4.H | V16.0.5.4.H | 2020-11-30 |  | Shipped | RonlerAcresOr
3002090673 | D23476 | NF3 | Nitrogen Trifluoride | TBD | NA | 172.19.8.57 | 172.19.8.58 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-250-NF3 | STANDARD+HEAT | V16.0.5.4.H | V16.0.5.4.H | 2022-02-16 |  | Shipped | ChandlerAz
3002158201 | D24528 | NF3 | Nitrogen Trifluoride | TBD | NA | 172.19.8.57 | 172.19.8.58 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-250-NF3 | STANDARD+HEAT | V16.0.6.5.H | V16.0.6.5.H | 2022-12-08 |  | Shipped | Ireland
3002111995 | D23370 | NF3 | Nitrogen Trifluoride | TBD | NA | 172.19.8.57 | 172.19.8.58 | 255.255.0.0 | 172.19.0.250 |  | DFS 1-250-NF3 | STANDARD+HEAT | V16.0.6.4.H | V16.0.6.4.H | 2022-10-26 |  | Shipped | Israel
Note on G2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: not defined by customer
Note on H2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: not defined by customer
Note on I2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: not defined by customer
Note on J2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: not defined by customer
Note on G3: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: not defined by customer
Note on H3: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: not defined by customer
Note on I3: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: not defined by customer
Note on J3: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: not defined by customer
Note on G4: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: not defined by customer
Note on H4: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: not defined by customer
Note on I4: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: not defined by customer
Note on J4: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: not defined by customer
Note on G5: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: not defined by customer
Note on H5: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: not defined by customer
Note on I5: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: not defined by customer
Note on J5: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: not defined by customer

## SA
PO | PROJECT | GAS | GAS NAME | BLDG | PLC HOSTNAME | PLC IP | HMI IP | Subnet Mask | Gateway | GC# | MODEL | PROGRAM | INSTALLED VER | WIP VER | DELIVERY | COMMISSIONED | STATUS | ProgSent | Notes
DEMO | D13819-001 | DCS | Dichlorosilane (DCS) |  |  | 172.19.9.131 | 172.19.9.132 | 255.255.0.0 | 172.19.0.250 |  | DFS 2-AX250-DCS-H | C1D2+HEAT | V15.0.4.112 | V16.0.3.113.H | 2019-04-18 |  | SHIPPED |  | Heat Panels and 1 zone of cylinders, Has N2/He blend purge. No Heav. C1D2 with Z purge and redundancy power
Note on G2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Not defined by customer
Note on I2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Not defined by customer
Note on J2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Not defined by customer

## SA FLX
PO | PROJECT | GAS | GAS NAME | BLDG | PLC HOSTNAME | PLC IP | HMI IP | Subnet Mask | Gateway | GC# | MODEL | PROGRAM | INSTALLED VER | WIP VER | DELIVERY | COMMISSIONED | STATUS | SHIPPED | ProgSent | Notes
NONE | D18763 | HPM | Chlorine Trifluoride |  |  | 172.19.0.162 | 172.19.0.163 | 255.255.0.0 | 172.19.0.250 |  | DFS | AcvFLX |  | V16.0.3.0 | 2021-04-01
Note on P1: Requested Date
Note on R1: QUOTED DESIGN LOADED SHIPPED
Note on S1: Actual date
Note on I2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Not defined by customer
Note on J2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Not defined by customer

## TI
PO | PROJECT | GAS | GAS NAME | FAB | PLC HOSTNAME | PLC IP | HMI IP | Subnet Mask | Gateway | GC# | MODEL | PROGRAM | INSTALLED VER | WIP VER | DELIVERY | COMMISSIONED | STATUS | SHIPPED | ProgSent | Notes
4514442337 | D22033-01A1 | HCL | Hydrochloric acid | RFAB2 |  | 172.19.81.153 | 172.19.81.152 | 255.255.248.0 | None |  | BSGS |  |  | V0.1 | 2022-09-30 |  | SHIPPED | 2022-10-07 |  | Stored on Copia. Version created 10/6/22.
4514442337 | D22033-01A2 | HCL | Hydrochloric acid | RFAB2 |  | 172.19.81.155 | 172.19.81.154 | 255.255.248.0 | None |  | BSGS |  |  | V0.1 | 2022-09-30 |  | SHIPPED | 2022-10-07 |  | Stored on Copia. Version created 10/6/22.
4514442337 | D22033-01A3 | HCL | Hydrochloric acid | RFAB2 |  | 172.19.81.157 | 172.19.81.156 | 255.255.248.0 | None |  | BSGS |  |  | V0.1 | 2022-09-30 |  | SHIPPED | 2022-10-07 |  | Stored on Copia. Version created 10/6/22.
4514442337 | D22033-01C1 | HCL | Hydrochloric acid | RFAB2 |  | 172.19.81.159 | 172.19.81.158 | 255.255.248.0 | None |  | GIB |  |  | V0.1 | 2022-09-30 |  | SHIPPED | 2022-10-07 |  | Stored on Copia. Version created 10/6/22.
4514442337 | D22033-01D1 | HCL | Hydrochloric acid | RFAB2 |  | 172.19.81.161 | 172.19.81.160 | 255.255.248.0 | None |  | GIB Sample |  |  | V0.1 | 2022-09-30 |  | SHIPPED | 2022-10-07 |  | Stored on Copia. Version created 10/6/22.
4514442337 | D22033-02A1 | NF3 | Nitrogen trifluoride | RFAB2 |  | 172.19.81.147 | 172.19.81.146 | 255.255.248.0 | None |  | BSGS |  |  | V0.1 | 2022-09-30 |  | SHIPPED | 2022-10-07 |  | Stored on Copia. Version created 10/6/22.
4514442337 | D22033-02A2 | NF3 | Nitrogen trifluoride | RFAB2 |  | 172.19.81.149 | 172.19.81.148 | 255.255.248.0 | None |  | BSGS |  |  | V0.1 | 2022-09-30 |  | SHIPPED | 2022-10-07 |  | Stored on Copia. Version created 10/6/22.
4514442337 | D22033-02C1 | NF3 | Nitrogen trifluoride | RFAB2 |  | 172.19.81.151 | 172.19.81.150 | 255.255.248.0 | None |  | GIB |  |  | V0.1 | 2022-09-30 |  | SHIPPED | 2022-10-07 |  | Stored on Copia. Version created 10/6/22.
4514442337 | D22033-03A1 | TCS | Trichlorosinane | RFAB2 |  | 172.19.81.163 | 172.19.81.162 | 255.255.248.0 | None |  | BSGS |  |  | V0.1 | 2022-09-30 |  | SHIPPED | 2022-10-07 |  | Stored on Copia. Version created 10/6/22.
4514442337 | D22033-03A2 | TCS | Trichlorosinane | RFAB2 |  | 172.19.81.165 | 172.19.81.164 | 255.255.248.0 | None |  | BSGS |  |  | V0.1 | 2022-09-30 |  | SHIPPED | 2022-10-07 |  | Stored on Copia. Version created 10/6/22.
4514442337 | D22033-03C1 | TCS | Trichlorosinane | RFAB2 |  | 172.19.81.167 | 172.19.81.166 | 255.255.248.0 | None |  | GIB |  |  | V0.1 | 2022-09-30 |  | SHIPPED | 2022-10-07 |  | Stored on Copia. Version created 10/6/22.
4515269470 | D27411-01A1 | HCL | Hydrochloric acid | DMOS6 |  | 172.19.81.153 | 172.19.81.152 | 255.255.248.0 | None |  | BSGS |  |  |  | 2024-02-08
4515269470 | D27411-01A2 | HCL | Hydrochloric acid | DMOS6 |  | 172.19.81.155 | 172.19.81.154 | 255.255.248.0 | None |  | BSGS |  |  |  | 2024-02-08
4515269470 | D27411-01A3 | HCL | Hydrochloric acid | DMOS6 |  | 172.19.81.157 | 172.19.81.156 | 255.255.248.0 | None |  | BSGS |  |  |  | 2024-02-08
4515269470 | D27411-01C1 | HCL | Hydrochloric acid | DMOS6 |  | 172.19.81.159 | 172.19.81.158 | 255.255.248.0 | None |  | GIB |  |  |  | 2024-02-08
4515269470 | D27411-01D1 | HCL | Hydrochloric acid | DMOS6 |  | 172.19.81.161 | 172.19.81.160 | 255.255.248.0 | None |  | GIB Sample |  |  |  | 2024-02-08
4515269470 | D27411-02A1 | NF3 | Nitrogen trifluoride | DMOS6 |  | 172.19.81.147 | 172.19.81.146 | 255.255.248.0 | None |  | BSGS |  |  |  | 2024-02-08
4515269470 | D27411-02A2 | NF3 | Nitrogen trifluoride | DMOS6 |  | 172.19.81.149 | 172.19.81.148 | 255.255.248.0 | None |  | BSGS |  |  |  | 2024-02-08
4515269470 | D27411-02C1 | NF3 | Nitrogen trifluoride | DMOS6 |  | 172.19.81.151 | 172.19.81.150 | 255.255.248.0 | None |  | GIB |  |  |  | 2024-02-08
4515269470 | D27411-03A1 | TCS | Trichlorosinane | DMOS6 |  | 172.19.81.163 | 172.19.81.162 | 255.255.248.0 | None |  | BSGS |  |  |  | 2024-02-08
4515269470 | D27411-03A2 | TCS | Trichlorosinane | DMOS6 |  | 172.19.81.165 | 172.19.81.164 | 255.255.248.0 | None |  | BSGS |  |  |  | 2024-02-08
4515269470 | D27411-03C1 | TCS | Trichlorosinane | DMOS6 |  | 172.19.81.167 | 172.19.81.166 | 255.255.248.0 | None |  | GIB |  |  |  | 2024-02-08
4515369584 | D27616-001 | NF3 | Nitrogen trifluoride | DMOS6 |  | 192.168.2.49 | 192.168.2.50 | 255.255.252.0 | None? |  | DFS 1-AX250-NF3 |  |  | G_G_B_0_C_PW_4E | 2023-05-09 |  | SHIPPED | 2023-05-15
4515402402 | D86793-02A1 | NF3 | Nitrogen trifluoride | [7 empty] | BSGS |  |  |  | 2023-11-27
4515402402 | D86793-02A2 | NF3 | Nitrogen trifluoride | [7 empty] | BSGS |  |  |  | 2023-11-27
4515402402 | D86793-02C1 | NF3 | Nitrogen trifluoride | [7 empty] | GIB |  |  |  | 2023-11-27
Note on P1: Requested Date
Note on R1: QUOTED DESIGN LOADED SHIPPED
Note on S1: Actual date

## Version Key
TIA VER |  | TIA SP |  | TIA UPD |  | REV#
V15 | . | 0 | . | 1 | . | 100

## OnSemi LDC
PO | PROJECT | LIQUID | PLC HOSTNAME | HMI HOSTNAME | PLC IP | HMI IP | Subnet Mask | Gateway | GC# | MODEL | PROGRAM | INSTALLED VER | WIP VER | DELIVERY | COMMISSIONED | STATUS | SHIPPED | ProgSent | Notes
10424443 | D26315-001 | Teos | D26315-001 | D26315-001-HMI | 10.104.179.131 | 10.104.179.132 | 255.255.255.0 |  |  | DFS 4-AX250-Teos | G_L_V_0_P_0_23 | e480fe89b9 |  | 2023-02-27 |  | SHIPPED | 2023-02-27
10428206 | D87497-001 | Teos |  | -HMI | [5 empty] | DFS 4-AX250-Teos |  |  |  | 2023-11-22
-HMI
-HMI
-HMI
-HMI
-HMI
Note on O1: Requested Date
Note on Q1: QUOTED DESIGN LOADED SHIPPED
Note on R1: Actual date

## Gasses
Name | Formula | Monitor ALL CAPS | Connection | Used
Argon(3.5%) / Xenon(10ppm) / Neon | Ar(3.5%)/ Xe(10ppm)/ Ne |  | CGA 718
Acetylene | C2H2 | C2H2 | CGA 510 | Y
Ammonia | NH3 |  | CGA 720
Boron Trichloride(.5%) / Helium | BCl3(0.5%)/He |  | CGA 634
Boron Trichloride | BCl3 | BCL3 | DISS 634 | Y
Boron Trifluoride | BF3 | BF3 | DISS 642 | Y
Carbon Monoxide | CO | CO | DISS 724 | Y
Carbonyl Sulfide | COS | COS | DISS 722 | Y
Chlorine | Cl2 | CL2 | DISS 728 | Y
Chlorine Trifluoride | ClF3 | CLF3 | DISS 728 | Y
Deuterium | D2 | D2 | DISS 728 | Y
Diborane(0.5%) / Helium | B2H6(0.5%)/He | B2H6/HE | DISS 632 | N
Diborane(10%) / Hydrogen | B2H6(10%)/H2 | B2H6/H2 | DISS 632 | Y
Diborane(15%) / Hydrogen Mixture | B2H6(15%)/H2 |  | CGA 632
Diborane(5%) / Helium | B2H6(5%)/He | B2H6/HE | DISS 632 | Y
Diborane(5%) / Nitrogen | B2H6(5%)/N2 | B2H6/N2 | DISS 632 | Y
Dichloromethaneide | CHCl2 | CHCL2 |  | Y
Dichlorosilane (DCS) | SiH2Cl2 | DCS | DISS 636 | Y
Difluoromethane | CH2F2 | CH2F2 | DISS 724 | Y
Disilane | Si2H6 | SI2H6 | DISS 636 | Y
Ethane | C2H6 | C2H6 | CGA 350 | Y
Ethylene | C2H4 | C2H4 | CGA 350 | Y
Ethylene(30%) / Helium | C2H4(30%) /He |  | N/A | Y
Fluorine(1% ) / Krypton(1.2%) / Neon | F2(1%) / 1.2%Kr / Ne |  | CGA 728
Fluorine(1% ) / Argon(3.5%) / Neon | F2(1%) / 3.5%Ar / Ne |  | CGA 728 10
Fluorine(20% ) / Nitrogen | F2(20%)/N2 | F2/N2 | CGA 679
Fluorine(<5%) / Nitrogen (HARTES) | F2(<5%)/N2 | F2/N2 | DISS 638 | Y
Fluorine(20%) / Argon | F2(20%)/Ar | F2/AR | DISS 638 | Y
Fluorine(20%) / Nitrogen | F2(20%)/N2 | F2/N2 | DISS 638 | Y
Fluoromethane (Halocarbon-41) | CH3F | CH3F | DISS 724 | Y
Germane(10%) / Hydrogen | GEH4(10%)/H2 | GEH4/H2 | DISS 632
Helium(1.2% ) / Nitrogen | He (1.2%) / N2 |  | N/A
Hexafluorocyclobutene | C4F6 | C4F6 | DISS 724 | Y
Hydrogen | H2 | H2 | DISS 724 | Y
Hydrogen(3.8% ) / Nitrogen | H2 (3.8%) / N2 |  | CGA 724
Hydrogen Bromide | HBr | HBR | DISS 634 | Y
Hydrogen Chloride | HCl | HCL | DISS 634 | Y
Hydrogen Fluoride | HF | HF | 1/4" FVCR | Y
Hydrogen Fluoride Heated | HF Heat | HF | DISS 638 | Y
Hydrogen Iodine | HI | HI |  | Y
Krypton(3.8%) / Neon | Kr |  | CGA 580
Methane | CH4 | CH4 | DISS 724 | Y
Methane(10%) / Argon (P10) | CH4(10%)/Ar | P-10 | DISS 724 | Y
Nitric Oxide | NO | NO | DISS 728 | Y
Nitrogen Trifluoride | NF3 | NF3 | DISS 640 | Y
Oxygen(0.5% ) / Helium | O2 (0.5%) / He |  | N/A
Oxygen(30%) / Helium | O2 (30%) / He |  | CGA 712
Phosphine(5%) / Helium | PH3(5%)/He | PH3/HE | DISS 632 | Y
Phosphine(10%) / Hydrogen | PH3(10%)/H2 | PH3/H2 | DISS 632
Phosphine(0.5%) / Nitrogen | PH3(0.5%)/N2 | PH3/N2 | DISS 632 | Y
Phosphine(5%) / Nitrogen | PH3(5%)/N2 | PH3/N2 | DISS 632 | Y
Phosphine(50vpm) / Nitrogen | PH3 50vppm in N2 |  | CGA 632
Phosphine(500vppm) / Nitrogen | PH3 500vppm / N2 |  | CGA 632
Propylene | C3H6 | C3H6 | CGA 510 | Y
Silane | SiH4 | SIH4 | DISS 632 | Y
Silicon Tetrachloride | SiCl4 |  | CGA 636 M
Silicon Tetrafluoride | SiF4 | SIF4 | DISS 642 | Y
Sulfur Dioxide | SO2 | SO2 | CGA 660 | Y
Tetraethyl orthosilicate | Si(OC2H5)4 | TEOS
TriFluoroIodoMethane | CF3I |  | N/A
Trifluoromethane | CHF3 |  | CGA 724
Trimethylsilane | TMS | TMS | DISS 632 | Y
Trisilylamine | TSA | TSA | DISS 632 | Y
Tungsten Hexafluoride | WF6 | WF6 | DISS 638 | Y
How to set subscript or superscript:
Highlight the characters and press Ctrl+1 then choose subscript.

## Check List
Update checklist
- | Before download of PLC
Confirm equipment and WIP program are a match: ASD, AX, …
Determine if equipment is offline or manually jumpered.
1 | Open Installed program.
2 | Go online.
3 | Select all data DBs, right click and select 'Snapshot of the actual values'.
4 | right click again and select 'Copy snapshots to start values/ Only retain values.
5 | Compile and save Installed copy. This is now a current 'as found' program.
6 | Open WIP program
- | If WIP program can go online with PLC
1 | Go online with WIP program.
2 | Select all data DBs, right click and select 'Snapshot of the actual values'.
3 | right click again and select 'Copy snapshots to start values/ Only retain values.
4 | Compile and save WIP program. Skip to After download of PLC
OR | If WIP program can't go online with PLC
1 | Compare (offline)Installed program to WIP to determine if data DB's are the same.
- | IF data DBs are the same.
2 | Copy desired data DBs from Installed program to WIP program, using reference projects.
- | IF Installed and WIP are on the different FW, update PLC firmware.
3 | Compile and save WIP program. Skip to After download of PLC
OR | IF data DBs are different
1 | Copy desired data DBs from Installed program to excel
2 | Open WIP copy of program
3 | Manually set values to match excel copy
- | After download of PLC
1 | Update HMI as needed. Confirm Doc Software screen is current.
2 | Pull USB Flash and verify data is readable and manual is latest.
3 | Confirm HMI shows correct date/time.
- | Record keeping
1 | Move Installed PLC program to C:\Installed\Archive.
2 | Save WIP PLC program to Installed folder.
3 | Archive WIP program for Customer and DFS records.
4 | email archive to customer
5 | Update Project folder records.
6 | Update ACvFlo master list.xlsx (this file)
Draft Only